## 日越比較
|  |  | Vietnamese industrial wastewater standard | [5 empty] | Japan uniform drainage standard (Ministry of the Environment)
|  |  | Vietnamese standard (encouraging compliance) |  | National Technical Regulations (Regulatory Basis)
|  |  | TCVN5945:2010 |  | QCVN 24:2009 |  | QCVN 40:2011
| project | unit |  |  | C value |  | C value |  |  |  | Analysis
|  |  | A | B | A | B | A | B |  |  | QCVN 40: 2011 (QVCN24: 2009 and reference)
1 | Temperature | oC | 40 | 40 | 40 | 40 | 40 | 40 | - |  | TCVN 4557: 1988 Water quality - Method for dertermination of temperature
- | Odor |  | Not uncomfortable | Not uncomfortable | Not uncomfortable | Not uncomfortable | - | - | -
2 | Colour | 度 | 20 | 70 | 20 | 70 | 50 | 150 | - |  | TCVN 6185:2015 Water quality - Examination and determination of color
| Identify | Correct | Co-Pt2, pH7 |  |  |  | Co-Pt, pH7
3 | pH | - | 6 - 9 | 5.5 - 9 | 6 - 9 | 5.5 - 9 | 6 - 9 | 5.5 - 9 | 5.8 - 8.6 (river) 5.0 - 9.0 (marine area) |  | TCVN 6492: 2011 (ISO 10523: 2008) Water quality -- Determination of pH
4 | BOD5 (20oC) | mg/l | 30 | 50 | 30 | 50 | 30 | 50 | 160 Day average 120 |  | TCVN 6001 - 1: 2008 (ISO 5815 - 1: 2003) Water quality - Determination of biochemical oxygen demand after n days (BODn) -- Part 1: Dilution and seeding method with allylthiourea addition
5 | COD Cr | mg/l | 50 | 100 | 50 | 100 | 75 | 150 | 160 Day average 120 | CODMn | TCVN 6491: 1999 (ISO 6060: 1989) Water quality - Determination of the chemical oxygen demand
6 | TSS | mg/l | 50 | 100 | 50 | 100 | 50 | 100 | 200 Day average 150 |  | TCVN 6625: 2000 (ISO 11923: 1997) Water quality - Determination of suspended solids by filtration through glass-fibre filters
7 | As | mg/l | 0.05 | 0.1 | 0.05 | 0.1 | 0.05 | 0.1 | 0.1 |  | TCVN 6626: 2000 Water quality - Determination arsenic - Atomic absorption spectrometric method (hydride technique)
8 | Hg | mg/l | 0.005 | 0.01 | 0.005 | 0.01 | 0.005 | 0.01 | 0.005 | Mercury and alkyl mercury and other mercury compounds | TCVN 7877: 2008 (ISO 5666-1999) Water quality – Determination of mercury
[9 empty] | Not to be detected | Alkyl mercury compound
9 | Pb | mg/l | 0.1 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 | 0.1 |  | TCVN 6193: 1996 Water quality – Determination of cobalt nickel, copper, zinc, cadmium, and lead. Flame atomic absorption spectrometric methods
10 | Cd | mg/l | 0.1 | 0.2 | 0.005 | 0.01 | 0.05 | 0.1 | 0.03 |  | TCVN 6193: 1996 Water quality – Determination of cobalt nickel, copper, zinc, cadmium, and lead. Flame atomic absorption spectrometric methods
11 | Cr6+ | mg/l | 0.05 | 0.1 | 0.05 | 0.1 | 0.05 | 0.1 | 0.5 | mg-Cr(VI)/L | TCVN 6658: 2000 (JSA ISO 11083: 1994) Water quality – Determination of chromium (VI). Spectrometric method using 1,5-diphenylcarbazide
12 | Cr3+ | mg/l | 0.2 | 1 | 0.2 | 1 | 0.2 | 1 | - |  | TCVN 6222: 2008 Water quality- Determination of chromium - Atomic absorption spectrometric method
- | [8 empty] | 2 | Cr含有量 (mg/L)
13 | Cu | mg/l | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  | TCVN 6193: 1996 Water quality – Determination of cobalt nickel, copper, zinc, cadmium, and lead. Flame atomic absorption spectrometric methods
14 | Zn | mg/l | 3 | 3 | 3 | 3 | 3 | 3 | 2 |  | TCVN 6193: 1996 Water quality – Determination of cobalt nickel, copper, zinc, cadmium, and lead. Flame atomic absorption spectrometric methods
15 | Ni | mg/l | 0.2 | 0.5 | 0.2 | 0.5 | 0.2 | 0.5 | - |  | TCVN 6193: 1996 Water quality – Determination of cobalt nickel, copper, zinc, cadmium, and lead. Flame atomic absorption spectrometric methods
16 | Mn | mg/l | - | - | 0.5 | 1 | 0.5 | 1 | 10 | Soluble manganese | TCVN 6002: 1995 Water quality – Determination of manganese - Formaldoxime spectrometric method
17 | Fe | mg/l | - | - | 1 | 5 | 1 | 5 | 10 | Solubility of iron | TCVN 6177: 1996 (ISO 6332-1988) Water quality – Determination of iron - Spectrometric method using 1,10-phenantrolin TCVN 6665: 2011 (ISO 11885: 2007) Water quality -- Determination of selected elements by inductively coupled plasma optical emission spectrometry (ICP-OES)
- | Tin | mg/l | - | - | 0.2 | 1 | - | - | -
18 | Total cyanide | mg/l | 0.07 | 0.1 | 0.07 | 0.1 | 0.07 | 0.1 | 1 | mg-CN/L | TCVN 6181: 1996 (ISO 6703-1-1984) Water quality - Determination of total cyanide
19 | Total phenol | mg/l | 0.1 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 | 5 |  | TCVN 6216: 1996 (ISO 6439-1990) Water quality -- Determination of phenol index -- 4-Aminoantipyrine spectrometric methods after distillation TCVN 6199-1: 1995 (ISO 8165/1: 1992) Water quality -- Determination of selected monovalent phenols -- Part 1: Gas-chromatographic method after enrichment by extraction
20 | Mineral oil | mg/l | 1 | 5 | 5 | 5 | 5 | 10 | 5 | Normal hexane extract substance content (mineral oil content) | TCVN 5070: 1995 Water quality - Weight method for determination of oil and oil product
- | Fats and oils (animal and vegetable oils) | mg/l | - | - | 10 | 20 | - | - | 30 | Normal hexane extract substance content (animal and vegetable fat and oil content) | TCVN 7875: 2008 Water - Determination of oil and grease - Partition-infrared method United States Environmental Protection Agency (EPA) Analysis Method 1664 Measurement of total fats and oils based on extracted weight method (fats and oils and total petroleum hydrocarbons)
21 | Sulfur compounds | mg/l | 0.2 | 0.5 | 0.2 | 0.5 | 0.2 | 0.5 | - |  | TCVN 6637: 2000 (ISO 10530: 1992) Water quality - Determination of dissolved sulfide - Photometric method using methylene blue
22 | Fluoride | mg/l | - | - | 5 | 10 | 5 | 10 | 8 (public waters) 16 (Sea) | Fluorine and its compounds | TCVN 6494-1: 2011 (ISO 10304-1: 2007) Water quality -- Determination of dissolved anions by liquid chromatography of ions -- Part 1: Determination of bromide, chloride, fluoride, nitrate, nitrite, phosphate and sulfate
23 | NH4+-N | mg/l | 5 | 10 | 5 | 10 | 5 | 10 | - | 100mg / l (NH4 + -N × 0.4 + Ammonium Nitric acid Chicken + nitric acid Chicken) | TCVN 5988: 1995 (ISO 5664: 1984) Water quality -- Determination of ammonium -- Distillation and titration method TCVN 6620: 2000 Water quality - Determination of ammonium - Potentiometric method
24 | T-N | mg/l | 15 | 30 | 15 | 30 | 20 | 40 | 120 Day average 60 |  | TCVN 6638: 2000 Water quality - Determination of nitrogen - Catalytic digestion after reduction with devarda's alloy
25 | T-P | mg/l | 4 | 6 | 4 | 6 | 4 | 6 | 16 Day average 8 |  | TCVN 6202: 2008 (ISO 6878: 2004) Water quality -- Determination of phosphorus -- Ammonium molybdate spectrometric method
26 | Chloride | mg/l | 500 | 600 | 500 | 600 | 500 | 1000 | - |  | TCVN 6494-1: 2011 (ISO 10304-1: 2007) Water quality -- Determination of dissolved anions by liquid chromatography of ions -- Part 1: Determination of bromide, chloride, fluoride, nitrate, nitrite, phosphate and sulfate
not applicable when discharging into saline water and brackish water
27 | Residual chlorine | mg/l | 1 | 2 | 1 | 2 | 1 | 2 | - |  | TCVN 6225-3: 2011 (ISO 7393-3: 1990) Water quality - Determination of free chlorine and total chlorine - Part 3: Iodometric titration method for the determination of total chlorine
28 | Pesticide: Organic chlorine | mg/l | undetected | undetected | 0.1 | 0.1 | 0.05 | 0.1 | Specified for each substance |  | TCVN 7876: 2008 Water - Determination of organochlorine pesticides content. Liquid-liquid extraction gas chromatographic method
29 | Pesticide: Organic phosphorus | mg/l | undetected | undetected | 0.3 | 1 | 0.3 | 1 | 1 | As an organophosphorus compound | TCVN 8062: 2009 Organophosphorus compounds by gas chromatography - Capillary column technique
30 | T-PCB | mg/l | - | - | 0.003 | 0.01 | 0.003 | 0.01 | 0.003
31 | Coliform | MPN/100ml | 3000 | 5000 | 3000 | 5000 | 3000 | 5000 | 3000 / cm3 | Day average | TCVN 8775: 2011 - Water quality - Total coliform - Membrane-filter technique TCVN 6187 - 1: 2009 (ISO 9308 - 1: 2000) Water quality - Detection and enumeration of Escherichia coli and coliform bacteria - Part 1: Membrane filtration method TCVN 6187-2: 1996 (ISO 9308-2: 1990 (E)) Water quality - Detection and enumeration if coliform organisms, thermotolerant coliform organisms, and presumptive Escherichia coli - Part 2: Multiple tube (most probable number) method
32 | Gross α activity | Bq/l | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - |  | TCVN 6053: 2011 Water quality - Measurement of gross alpha activity in non-saline water - Thick source method
33 | Gross β activity | Bq/l | 1 | 1 | 1 | 1 | 1 | 1 | - |  | TCVN 6219:2011 Water quality - Measurement of gross beta activity in non-saline water - Thick source method
- | Organic insecticide | mg/l | - | - | - | - | - | - | -
- | Organochlorine insecticide | mg/l | - | - | - | - | - | - | -
- | Measurement by biological indicator | - | - |  | - | - | - | - | -
34 | Vibrio fishcheri (Luminescent bacteria test) | mg/l | TU (Toxicity Units) 8 |  | - | - | - | -
QCVN | [5 empty] | TCVN |  |  |  |  | Other
A: Value of pollutants in industrial wastewater discharged to water used for daily use water | [5 empty] | A standard or less: It can be discharged to the water area that is constantly used for living purposes |  |  |  |  | TCVN 6663 - 1: 2011 (ISO 5667 - 1: 2006) Water quality -- Sampling -- Part 1: Guidance on the design of sampling programmes and sampling techniques
B: Contaminant value in industrial wastewater discharged to water bodies other than daily use water | [5 empty] | B standard or less: Excluding daily life waters, other drains can be discharged into water bodies discharged. |  |  |  |  | TCVN 6663-3: 2008 (ISO 5667-3: 2003) Water quality - Sampling. Guidance on the preservation and handling of water samples
[6 empty] | C standard or less: Can be discharged to specified places (drainage reservoirs installed individually, water supply pipes to centralized wastewater treatment facilities, etc.). |  |  |  |  | TCVN 5999: 1995 (ISO 5667-10: 1992) Water quality - Sampling - Part 10: Guidance on sampling of wastewaters
reference | About TCVN 5945: 2005 |  | https://www.env.go.jp/air/tech/ine/asia/vietnam/files/needs/needs.pdf
| About QCVN 24: 2009 |  | https://www.env.go.jp/air/tech/ine/asia/vietnam/files/pollution/pollution.pdf
| QCVN 24: 2009 (Japanese translation) |  | https://www.env.go.jp/air/tech/ine/asia/vietnam/files/law/V28.pdf