## Drawing
THAI BINH 2 THERMAL POWER PLANT
DRAWING OF MEASURING POINT
ESP
Gas direction
| INLET - Duct A |  | INLET - Duct B
Gas direction
| OUTLET - Duct A |  | OUTLET - Duct B
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000

## IN-A
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-21 | [10 empty] | Measuring condition | [7 empty] | 100% Load
Measuring position | [5 empty] | Unit 2 ESP Inlet A side | [10 empty] | Measuring person | [7 empty] | Morimoto, Dung
[12 empty] | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by | [15 empty] | Customer
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  |  | 101.1
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 15:25 |  |  |  |  | 11 |  |  |  | 10 | [5 empty] | 27 |  |  | 0 |  |  |  |  | 0.6822 |  |  |  |  | 8.8 |  |  |  | 8.8 |  |  | 3.57
|  |  | 15:33 |  |  |  |  | 12 |  |  |  | 10 | [5 empty] | 27 |  |  | 0 |  |  |  |  | 0.6733 |  |  |  |  | 8.7 | [6 empty] | 3.57
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | D2 －013 －090 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －002
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/m3N
| C-2 |  | 15:24 |  |  |  |  | 14.2 |  |  |  |  | 5.8 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2017
|  |  | 15:33 |  |  |  |  | 14.2 |  |  |  |  | 5.8 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2017
|  |  | Average |  |  |  |  | 14.2 |  |  |  |  | 5.8 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －001
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 15:08 | [5 empty] | 168 | [5 empty] | 144 |  |  |  |  | -2.4 | [5 empty] | 19.9 | [5 empty] | 0.848 |  |  |  | #NAME?
| A-2 | [6 empty] | 92 | [5 empty] | 145 | [10 empty] | 14.7 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 165 | [5 empty] | 144 | [10 empty] | 19.7 | [7 empty] | QA
| B-1 | [6 empty] | 56 | [5 empty] | 144 | [10 empty] | 11.5 | [7 empty] | m3/h
| B-2 | [6 empty] | 196 | [5 empty] | 145 | [10 empty] | 21.5 | [5 empty] | ① |  | 787000
| B-3 | [6 empty] | 60 | [5 empty] | 142 | [10 empty] | 11.9 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 80 | [5 empty] | 139 | [10 empty] | 13.7 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 75 | [5 empty] | 138 | [10 empty] | 13.3 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 80 | [5 empty] | 138 | [10 empty] | 13.7 | [7 empty] | m3N/h
| D-1 | [6 empty] | 74 | [5 empty] | 134 | [10 empty] | 13.2 | [5 empty] | ① |  | 556000
| D-2 | [6 empty] | 198 | [5 empty] | 132 | [10 empty] | 21.6 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 68 | [5 empty] | 133 | [10 empty] | 12.7 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 148 | [5 empty] | 129 | [10 empty] | 18.7 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 115 | [5 empty] | 128 | [10 empty] | 16.5 | [7 empty] | m3N/h
| E-3 | 15:21 | [5 empty] | 182 | [5 empty] | 129 | [10 empty] | 20.7 | [5 empty] | ① |  | 507000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 138 |  | #DIV/0! | [8 empty] | 16.2 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 004 |  |  |  | Thermometer | [7 empty] | DVM － 010 －005
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －020
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －024
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical room | [5 empty] | TEC-G-QT-001-003 (01) | [6 empty] | Revised (Enacted) date | [5 empty] | 2015-04-01

## IN-B
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-21 | [10 empty] | Measuring condition | [7 empty] | 100% Load
Measuring position | [5 empty] | Unit 2 ESP Inlet B side | [10 empty] | Measuring person | [7 empty] | Morimoto, Dung
[12 empty] | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by | [15 empty] | Customer
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  |  | 101.1
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 15:50 |  |  |  |  | 14 |  |  |  | 10 | [5 empty] | 27 |  |  | 0 |  |  |  |  | 0.6714 |  |  |  |  | 8.7 |  |  |  | 8.8 |  |  | 3.57
|  |  | 16:00 |  |  |  |  | 15 |  |  |  | 10 | [5 empty] | 27 |  |  | 0 |  |  |  |  | 0.6784 |  |  |  |  | 8.8 | [6 empty] | 3.57
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | D2 －013 －085 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －007
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/m3N
| C-2 |  | 15:49 |  |  |  |  | 14 |  |  |  |  | 6 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2008
|  |  | 16:10 |  |  |  |  | 14.1 |  |  |  |  | 5.9 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2012
|  |  | Average |  |  |  |  | 14.1 |  |  |  |  | 6 |  |  |  | - | [5 empty] | 79.9 |  |  |  |  | 1.2
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －001
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 14:50 | [5 empty] | 172 | [5 empty] | 126 |  |  |  |  | -2.5 | [5 empty] | 20.1 | [5 empty] | 0.855 |  |  |  | #NAME?
| A-2 | [6 empty] | 105 | [5 empty] | 125 | [10 empty] | 15.7 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 175 | [5 empty] | 127 | [10 empty] | 20.2 | [7 empty] | QA
| B-1 | [6 empty] | 66 | [5 empty] | 129 | [10 empty] | 12.4 | [7 empty] | m3/h
| B-2 | [6 empty] | 205 | [5 empty] | 129 | [10 empty] | 21.9 | [5 empty] | ① |  | 792000
| B-3 | [6 empty] | 63 | [5 empty] | 130 | [10 empty] | 12.1 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 84 | [5 empty] | 136 | [10 empty] | 14 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 75 | [5 empty] | 136 | [10 empty] | 13.2 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 82 | [5 empty] | 136 | [10 empty] | 13.8 | [7 empty] | m3N/h
| D-1 | [6 empty] | 58 | [5 empty] | 140 | [10 empty] | 11.6 | [5 empty] | ① |  | 565000
| D-2 | [6 empty] | 205 | [5 empty] | 140 | [10 empty] | 21.9 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 74 | [5 empty] | 135 | [10 empty] | 13.2 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 164 | [5 empty] | 141 | [10 empty] | 19.6 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 110 | [5 empty] | 139 | [10 empty] | 16 | [7 empty] | m3N/h
| E-3 | 15:05 | [5 empty] | 158 | [5 empty] | 137 | [10 empty] | 19.2 | [5 empty] | ① |  | 515000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 134 |  | #DIV/0! | [8 empty] | 16.3 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 003 |  |  |  | Thermometer | [7 empty] | DVM － 010 －004
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －020
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －024
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical room | [5 empty] | TEC-G-QT-001-003 (01) | [6 empty] | Revised (Enacted) date | [5 empty] | 2015-04-01

## Dust IN-A
MEASURING DATA SHEET (2) | [14 empty] | Customer | [9 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-21 | [11 empty] | Measuring condition | [5 empty] | 100% Load
Measuring position | [6 empty] | Unit 2 ESP Inlet A side | [11 empty] | Measuring person | [5 empty] | Morimoto
| DUST CONCENTRATION IN FLUE GAS | [21 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| □ | Form 1 |  | □ |  | Form 2 |  |  | ■ | Form 1 |  |  |  | □ |  | Form 2
| □ | QMA |  | □ |  | PF-020 |  |  | ■ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [10 empty] | Pa |  |  | kPa |  | 101.1
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [10 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [7 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  | kPa |  |  | m3N |  |  | g |  |  |  | g/m3N |  |  | g/m3N |  | %
| A-1~3 |  | 17:36 |  | 3 |  | 5 |  | 38 |  |  | 9 |  |  | 131 |  |  | 25 |  | 0.1 |  |  | 0.127 |  |  | 4.7874 |  |  |  | 37.7 |  |  | - |  | - |  | 3.17
| B-1~3 |  | 17:23 |  | 3 |  | 5 |  | 100 |  |  | 9 |  |  | 111 |  |  | 25 |  | 0.1 |  |  | 0.107 |  |  | 4.1107 |  |  |  | 38.4 |  |  | - |  | - |  | 3.17
| C-1~3 |  | 17:10 |  | 3 |  | 5 |  | 99 |  |  | 9 |  |  | 102 |  |  | 25 |  | 0.1 |  |  | 0.099 |  |  | 3.2805 |  |  |  | 33.1 |  |  | - |  | - |  | 3.17
| D-1~3 |  | 16:57 |  | 3 |  | 5 |  | 10 |  |  | 9 |  |  | 115 |  |  | 26 |  | 0.1 |  |  | 0.111 |  |  | 3.5642 |  |  |  | 32.1 |  |  | - |  | - |  | 3.36
| E-1~3 |  | 16:45 |  | 3 |  | 5 |  | 9 |  |  | 9 |  |  | 135 |  |  | 26 |  | 0.1 |  |  | 0.13 |  |  | 4.1492 |  |  |  | 31.9 |  |  | - |  | - |  | 3.36
[26 empty] | Average |  |  |  | 34.6 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | D2 － 013 －090 | [10 empty] | Suction pump | [6 empty] | DVM － 027 －002
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[23 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [9 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [20 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [7 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [6 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [9 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical room |  |  |  |  | TEC-G-QT-001-003 (01) |  |  |  |  | Revised (Enacted) date | [6 empty] | 2015-04-01

## Dust IN-B
MEASURING DATA SHEET (2) | [14 empty] | Customer | [9 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-21 | [11 empty] | Measuring condition | [5 empty] | 100% Load
Measuring position | [6 empty] | Unit 2 ESP Inlet B side | [11 empty] | Measuring person | [5 empty] | Dung
| DUST CONCENTRATION IN FLUE GAS | [21 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| □ | Form 1 |  | □ |  | Form 2 |  |  | ■ | Form 1 |  |  |  | □ |  | Form 2
| □ | QMA |  | □ |  | PF-020 |  |  | ■ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [10 empty] | Pa |  |  | kPa |  | 101.1
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [10 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [7 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  | kPa |  |  | m3N |  |  | g |  |  |  | g/m3N |  |  | g/m3N |  | %
| A-1~3 |  | 17:40 |  | 3 |  | 5 |  | 89 |  |  | 9 |  |  | 135 |  |  | 26 |  | 0.1 |  |  | 0.13 |  |  | 4.0286 |  |  |  | 31 |  |  | - |  | - |  | 3.36
| B-1~3 |  | 17:27 |  | 3 |  | 5 |  | 88 |  |  | 9 |  |  | 114 |  |  | 26 |  | 0.1 |  |  | 0.11 |  |  | 3.7323 |  |  |  | 33.9 |  |  | - |  | - |  | 3.36
| C-1~3 |  | 17:15 |  | 3 |  | 5 |  | 87 |  |  | 9 |  |  | 100 |  |  | 26 |  | 0.1 |  |  | 0.096 |  |  | 3.0206 |  |  |  | 31.5 |  |  | - |  | - |  | 3.36
| D-1~3 |  | 17:00 |  | 3 |  | 5 |  | 70 |  |  | 9 |  |  | 112 |  |  | 26 |  | 0.1 |  |  | 0.108 |  |  | 4.2419 |  |  |  | 39.3 |  |  | - |  | - |  | 3.36
| E-1~3 |  | 16:45 |  | 3 |  | 5 |  | 69 |  |  | 9 |  |  | 133 |  |  | 26 |  | 0.1 |  |  | 0.128 |  |  | 4.6308 |  |  |  | 36.2 |  |  | - |  | - |  | 3.36
[26 empty] | Average |  |  |  | 34.4 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | D2 － 013 －085 | [10 empty] | Suction pump | [6 empty] | DVM － 027 －007
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[23 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [9 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [20 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [7 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [6 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [9 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical room |  |  |  |  | TEC-G-QT-001-003 (01) |  |  |  |  | Revised (Enacted) date | [6 empty] | 2015-04-01

## OUT-A
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-21 | [10 empty] | Measuring condition | [7 empty] | 100% Load
Measuring position | [5 empty] | Unit 2 ESP Outlet A side | [10 empty] | Measuring person | [7 empty] | Hoai, Tuyen, Khanh
[12 empty] | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by | [15 empty] | Customer
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  |  | 101.1
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 15:28 |  |  |  |  | 1 |  |  |  | 10 | [5 empty] | 24 |  |  | 0 |  |  |  |  | 0.6855 |  |  |  |  | 8.7 |  |  |  | 8.8 |  |  | 2.99
|  |  | 15:36 |  |  |  |  | 2 |  |  |  | 10 | [5 empty] | 24 |  |  | 0 |  |  |  |  | 0.6889 |  |  |  |  | 8.8 | [6 empty] | 2.99
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | DVM －013 －004 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －010
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/m3N
| C-2 |  | 15:26 |  |  |  |  | 14.3 |  |  |  |  | 5.7 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2021
|  |  | 15:45 |  |  |  |  | 14.2 |  |  |  |  | 5.8 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2017
|  |  | Average |  |  |  |  | 14.3 |  |  |  |  | 5.8 |  |  |  | - | [5 empty] | 79.9 |  |  |  |  | 1.2
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －001
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 15:10 | [5 empty] | 108 | [5 empty] | 137 |  |  |  |  | -2.4 | [5 empty] | 15.8 | [5 empty] | 0.86 |  |  |  | #NAME?
| A-2 | [6 empty] | 104 | [5 empty] | 138 | [10 empty] | 15.6 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 114 | [5 empty] | 131 | [10 empty] | 16.3 | [7 empty] | QA
| B-1 | [6 empty] | 96 | [5 empty] | 138 | [10 empty] | 14.9 | [7 empty] | m3/h
| B-2 | [6 empty] | 126 | [5 empty] | 135 | [10 empty] | 17.1 | [5 empty] | ① |  | 768000
| B-3 | [6 empty] | 98 | [5 empty] | 126 | [10 empty] | 15.1 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 94 | [5 empty] | 137 | [10 empty] | 14.8 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 104 | [5 empty] | 133 | [10 empty] | 15.6 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 106 | [5 empty] | 127 | [10 empty] | 15.7 | [7 empty] | m3N/h
| D-1 | [6 empty] | 110 | [5 empty] | 135 | [10 empty] | 16 | [5 empty] | ① |  | 550000
| D-2 | [6 empty] | 134 | [5 empty] | 131 | [10 empty] | 17.7 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 108 | [5 empty] | 127 | [10 empty] | 15.8 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 112 | [5 empty] | 130 | [10 empty] | 16.1 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 92 | [5 empty] | 126 | [10 empty] | 14.6 | [7 empty] | m3N/h
| E-3 | 15:25 | [5 empty] | 108 | [5 empty] | 126 | [10 empty] | 15.8 | [5 empty] | ① |  | 502000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 132 |  | #DIV/0! | [8 empty] | 15.8 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 004 |  |  |  | Thermometer | [7 empty] | DVM － 010 －005
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －024
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －026
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical room | [5 empty] | TEC-G-QT-001-003 (01) | [6 empty] | Revised (Enacted) date | [5 empty] | 2015-04-01

## OUT-B
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-21 | [10 empty] | Measuring condition | [7 empty] | 100% Load
Measuring position | [5 empty] | Unit 2 ESP Outlet B side | [10 empty] | Measuring person | [7 empty] | Hoai, Tuyen, Khanh
[12 empty] | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by | [15 empty] | Customer
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  |  | 101.1
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 15:54 |  |  |  |  | 3 |  |  |  | 10 | [5 empty] | 25 |  |  | 0 |  |  |  |  | 0.6704 |  |  |  |  | 8.6 |  |  |  | 8.7 |  |  | 3.17
|  |  | 16:02 |  |  |  |  | 8 |  |  |  | 10 | [5 empty] | 25 |  |  | 0 |  |  |  |  | 0.6798 |  |  |  |  | 8.7 | [6 empty] | 3.17
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | DVM －013 －003 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －009
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/m3N
| C-2 |  | 15:52 |  |  |  |  | 14.1 |  |  |  |  | 5.9 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2018
|  |  | 16:03 |  |  |  |  | 14.1 |  |  |  |  | 5.9 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2018
|  |  | Average |  |  |  |  | 14.1 |  |  |  |  | 5.9 |  |  |  | - | [5 empty] | 80 |  |  |  |  | 1.2
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －003
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 14:50 | [5 empty] | 132 | [5 empty] | 126 |  |  |  |  | -2.6 | [5 empty] | 17.4 | [5 empty] | 0.867 |  |  |  | #NAME?
| A-2 | [6 empty] | 126 | [5 empty] | 124 | [10 empty] | 17 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 124 | [5 empty] | 123 | [10 empty] | 16.9 | [7 empty] | QA
| B-1 | [6 empty] | 118 | [5 empty] | 130 | [10 empty] | 16.5 | [7 empty] | m3/h
| B-2 | [6 empty] | 156 | [5 empty] | 127 | [10 empty] | 19 | [5 empty] | ① |  | 831000
| B-3 | [6 empty] | 120 | [5 empty] | 124 | [10 empty] | 16.6 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 118 | [5 empty] | 134 | [10 empty] | 16.5 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 116 | [5 empty] | 128 | [10 empty] | 16.4 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 118 | [5 empty] | 122 | [10 empty] | 16.5 | [7 empty] | m3N/h
| D-1 | [6 empty] | 116 | [5 empty] | 134 | [10 empty] | 16.4 | [5 empty] | ① |  | 600000
| D-2 | [6 empty] | 154 | [5 empty] | 131 | [10 empty] | 18.8 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 112 | [5 empty] | 123 | [10 empty] | 16.1 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 136 | [5 empty] | 133 | [10 empty] | 17.7 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 126 | [5 empty] | 132 | [10 empty] | 17 | [7 empty] | m3N/h
| E-3 | 15:03 | [5 empty] | 132 | [5 empty] | 127 | [10 empty] | 17.4 | [5 empty] | ① |  | 548000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 128 |  | #DIV/0! | [8 empty] | 17.1 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 004 |  |  |  | Thermometer | [7 empty] | DVM － 010 －005
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －024
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －026
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical room | [5 empty] | TEC-G-QT-001-003 (01) | [6 empty] | Revised (Enacted) date | [5 empty] | 2015-04-01

## Dust OUT-A
MEASURING DATA SHEET (2) | [14 empty] | Customer | [9 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-21 | [11 empty] | Measuring condition | [5 empty] | 100% Load
Measuring position | [6 empty] | Unit 2 ESP Outlet A side | [11 empty] | Measuring person | [5 empty] | Hoai
| DUST CONCENTRATION IN FLUE GAS | [21 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| ■ | Form 1 |  | □ |  | Form 2 |  |  | □ | Form 1 |  |  |  | □ |  | Form 2
| ■ | QMA |  | □ |  | PF-020 |  |  | □ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [10 empty] | Pa |  |  | kPa |  | 101.1
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [10 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [7 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  | kPa |  |  | m3N |  |  | g |  |  |  | g/m3N |  |  | g/m3N |  | %
| A-1~3 |  | 17:55 |  | 3 |  | 5 |  | 677 |  |  | 15 |  |  | 187 |  |  | 22 |  | 0.1 |  |  | 0.184 |  |  | 0.0043 |  |  |  | 0.0234 |  |  | - |  | - |  | 2.65
| B-1~3 |  | 17:36 |  | 3 |  | 5 |  | 676 |  |  | 15 |  |  | 189 |  |  | 23 |  | 0.1 |  |  | 0.185 |  |  | 0.00388 |  |  |  | 0.021 |  |  | - |  | - |  | 2.81
| C-1~3 |  | 16:35 |  | 3 |  | 5 |  | 57 |  |  | 15 |  |  | 182 |  |  | 23 |  | 0.1 |  |  | 0.178 |  |  | 0.0026 |  |  |  | 0.0146 |  |  | - |  | - |  | 2.81
| D-1~3 |  | 17:17 |  | 3 |  | 5 |  | 47 |  |  | 15 |  |  | 201 |  |  | 23 |  | 0.1 |  |  | 0.197 |  |  | 0.00334 |  |  |  | 0.017 |  |  | - |  | - |  | 2.81
| E-1~3 |  | 16:57 |  | 3 |  | 5 |  | 73 |  |  | 15 |  |  | 193 |  |  | 23 |  | 0.1 |  |  | 0.189 |  |  | 0.00491 |  |  |  | 0.026 |  |  | - |  | - |  | 2.81
[26 empty] | Average |  |  |  | 0.0204 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | DVM － 013 －004 | [10 empty] | Suction pump | [6 empty] | DVM － 027 －010
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[23 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [9 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [20 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [7 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [6 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [9 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical room |  |  |  |  | TEC-G-QT-001-003 (01) |  |  |  |  | Revised (Enacted) date | [6 empty] | 2015-04-01

## Dust OUT-B
MEASURING DATA SHEET (2) | [14 empty] | Customer | [9 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-21 | [11 empty] | Measuring condition | [5 empty] | 100% Load
Measuring position | [6 empty] | Unit 2 ESP Outlet B side | [11 empty] | Measuring person | [5 empty] | Tuyen, Khanh
| DUST CONCENTRATION IN FLUE GAS | [21 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| ■ | Form 1 |  | □ |  | Form 2 |  |  | □ | Form 1 |  |  |  | □ |  | Form 2
| ■ | QMA |  | □ |  | PF-020 |  |  | □ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [10 empty] | Pa |  |  | kPa |  | 101.1
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [10 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [7 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  | kPa |  |  | m3N |  |  | g |  |  |  | g/m3N |  |  | g/m3N |  | %
| A-1~3 |  | 17:58 |  | 3 |  | 5 |  | 23 |  |  | 15 |  |  | 212 |  |  | 24 |  | 0.1 |  |  | 0.206 |  |  | 0.00642 |  |  |  | 0.0312 |  |  | - |  | - |  | 2.99
| B-1~3 |  | 17:38 |  | 3 |  | 5 |  | 2 |  |  | 15 |  |  | 213 |  |  | 24 |  | 0.1 |  |  | 0.207 |  |  | 0.00443 |  |  |  | 0.0214 |  |  | - |  | - |  | 2.99
| C-1~3 |  | 17:17 |  | 3 |  | 5 |  | 20 |  |  | 15 |  |  | 202 |  |  | 24 |  | 0.1 |  |  | 0.196 |  |  | 0.00366 |  |  |  | 0.0187 |  |  | - |  | - |  | 2.99
| D-1~3 |  | 16:56 |  | 3 |  | 5 |  | 24 |  |  | 15 |  |  | 210 |  |  | 24 |  | 0.1 |  |  | 0.204 |  |  | 0.00568 |  |  |  | 0.0278 |  |  | - |  | - |  | 2.99
| E-1~3 |  | 16:35 |  | 3 |  | 5 |  | 15 |  |  | 15 |  |  | 194 |  |  | 24 |  | 0.1 |  |  | 0.189 |  |  | 0.00835 |  |  |  | 0.0442 |  |  | - |  | - |  | 2.99
[26 empty] | Average |  |  |  | 0.0287 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | DVM － 013 －003 | [10 empty] | Suction pump | [6 empty] | DVM － 027 －009
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[23 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [9 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [20 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [7 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [6 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [9 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical room |  |  |  |  | TEC-G-QT-001-003 (01) |  |  |  |  | Revised (Enacted) date | [6 empty] | 2015-04-01

## Velocity Temp.
THAI BINH 2 THERMAL POWER PLANT
[17 empty] | DATE: |  |  |  | 21-Feb-2018
[17 empty] | CONDITION: |  |  |  | 100% Load
ESP FLUE GAS MEASUREMENT DATA SHEET
VELOCITY AND TEMPERATURE
Gas direction
| 19.9 |  | 11.5 |  | 13.7 |  | 13.2 |  | 18.7 |  |  |  |  | 20.1 |  | 12.4 |  |  | 14.0 |  |  | 11.6 |  | 19.6
|  | 144 |  | 144 |  | 139 |  | 134 |  | 129 |  |  |  |  | 126 |  |  | 129 |  | 136 |  |  | 140 |  | 141
| 14.7 |  | 21.5 |  | 13.3 |  | 21.6 |  | 16.5 |  |  |  |  | 15.7 |  | 21.9 |  |  | 13.2 |  |  | 21.9 |  | 16.0
|  | 145 |  | 145 |  | 138 |  | 132 |  | 128 |  |  |  |  | 125 |  |  | 129 |  | 136 |  |  | 140 |  | 139
| 19.7 |  | 11.9 |  | 13.7 |  | 12.7 |  | 20.7 |  |  |  |  | 20.2 |  | 12.1 |  |  | 13.8 |  |  | 13.2 |  | 19.2
|  | 144 |  | 142 |  | 138 |  | 133 |  | 129 |  |  |  |  | 127 |  |  | 130 |  | 136 |  |  | 135 |  | 137
| INLET - Duct A | [12 empty] | INLET - Duct B
Vel
| Velocity Average ： 16.2 m/s | [12 empty] | Velocity Average ： 16.3 m/s
| Temperature Average ： 138 ℃ | [11 empty] | Temp | Temperature Average ： 134℃
| Gas flow rate ： 556,000 m3N/h (Wet) | [12 empty] | Gas flow rate ： 565,000 m3N/h (Wet)
Gas direction
| 15.8 |  | 14.9 |  | 14.8 |  | 16.0 |  | 16.1 |  |  |  |  | 17.4 |  | 16.5 |  |  | 16.5 |  |  | 16.4 |  | 17.7
|  | 137 |  | 138 |  | 137 |  | 135 |  | 130 |  |  |  |  | 129 |  |  | 133 |  | 136 |  |  | 135 |  | 135
| 15.6 |  | 17.1 |  | 15.6 |  | 17.7 |  | 14.6 |  |  |  |  | 17 |  | 19 |  |  | 16.4 |  |  | 18.8 |  | 17
|  | 138 |  | 135 |  | 133 |  | 131 |  | 126 |  |  |  |  | 126 |  |  | 129 |  | 131 |  |  | 132 |  | 134
| 16.3 |  | 15.1 |  | 15.7 |  | 15.8 |  | 15.8 |  |  |  |  | 16.9 |  | 16.6 |  |  | 16.5 |  |  | 16.1 |  | 17.4
|  | 131 |  | 126 |  | 127 |  | 127 |  | 126 |  |  |  |  | 125 |  |  | 127 |  | 126 |  |  | 125 |  | 128
| OUTLET - Duct A | [12 empty] | OUTLET - Duct B
Vel
| Velocity Average ： 15.8 m/s | [12 empty] | Velocity Average ： 17.1 m/s
| Temperature Average ： 132 ℃ | [11 empty] | Temp | Temperature Average ： 128 ℃
| Gas flow rate ： 551,000 m3N/h (Wet) | [12 empty] | Gas flow rate ： 600,000 m3N/h (Wet)
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
500
1000
1000
3000

## DUST-RESULT
THAI BINH 2 THERMAL POWER PLANT | [5 empty] | DATE: | 21-Feb-2018
[6 empty] | CONDITION: | 100% Load
ESP FLUE GAS MEASUREMENT DATA SHEET
DUST CONCENTRATION
Gas direction
| INLET - Duct A |  |  |  | INLET - Duct B
| Average | g/m3N |  |  | Average |  |  | g/m3N
|  | Total Average |  | g/m3N
Gas direction
| OUTLET - Duct A |  |  |  | OUTLET - Duct B
| Average | g/m3N |  |  | Average |  |  | g/m3N
|  | Total Average |  | g/m3N
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
38.4
33.1
32.1
33.9
31.5
39.3
0.0210
0.0146
0.0170
0.0214
0.0187
0.0278
0.0287
0.0204
34.4
34.6
37.7
31.9
36.2
0.0312
0.0442
0.0260
0.0234
31.0
0.0246
34.5

## Dust OUT-A T-2
MEASURING DATA SHEET (2) | [14 empty] | Customer | [9 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-19 | [11 empty] | Measuring condition | [5 empty] | T-2 100% Load
Measuring position | [6 empty] | Unit 2 ESP Outlet A side | [11 empty] | Measuring person | [5 empty] | Dung
| DUST CONCENTRATION IN FLUE GAS | [21 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| ■ | Form 1 |  | □ |  | Form 2 |  |  | □ | Form 1 |  |  |  | □ |  | Form 2
| ■ | QMA |  | □ |  | PF-020 |  |  | □ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [10 empty] | Pa |  |  | kPa |  | 101.6
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [10 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [7 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  | kPa |  |  | m3N |  |  | g |  |  |  | g/m3N |  |  | g/m3N |  | %
| A~E-2 |  | 16:48 |  | 5 |  | 5 |  | 580 |  |  | 15 |  |  | 190 |  |  | 22 |  | 0.1 |  |  | 0.188 |  |  | 0.01308 |  |  |  | 0.0696 |  |  | - |  | - |  | 2.65
#N/A
#N/A
#N/A
#N/A
[26 empty] | Average |  |  |  | 0.0696 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | DVM － 013 －004 | [10 empty] | Suction pump | [6 empty] | DVM － 027 －010
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[23 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [9 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [20 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [7 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [6 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [9 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical room |  |  |  |  | TEC-G-QT-001-003 (01) |  |  |  |  | Revised (Enacted) date | [6 empty] | 2015-04-01

## Dust OUT-A T-3
MEASURING DATA SHEET (2) | [14 empty] | Customer | [9 empty] | THAI BINH 2 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-19 | [11 empty] | Measuring condition | [5 empty] | T-3 100% Load
Measuring position | [6 empty] | Unit 2 ESP Outlet A side | [11 empty] | Measuring person | [5 empty] | Dung
| DUST CONCENTRATION IN FLUE GAS | [21 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| ■ | Form 1 |  | □ |  | Form 2 |  |  | □ | Form 1 |  |  |  | □ |  | Form 2
| ■ | QMA |  | □ |  | PF-020 |  |  | □ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [10 empty] | Pa |  |  | kPa |  | 101.6
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [10 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [7 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  | kPa |  |  | m3N |  |  | g |  |  |  | g/m3N |  |  | g/m3N |  | %
| A~E-3 |  | 17:10 |  | 5 |  | 5 |  | 573 |  |  | 15 |  |  | 185 |  |  | 22 |  | 0.1 |  |  | 0.183 |  |  | 0.00694 |  |  |  | 0.0379 |  |  | - |  | - |  | 2.65
#N/A
#N/A
#N/A
#N/A
[26 empty] | Average |  |  |  | 0.0379 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | DVM － 013 －004 | [10 empty] | Suction pump | [6 empty] | DVM － 027 －010
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[23 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [9 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [20 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [7 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [6 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [9 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical room |  |  |  |  | TEC-G-QT-001-003 (01) |  |  |  |  | Revised (Enacted) date | [6 empty] | 2015-04-01

## DUST-RESULT-2
THAI BINH 2 THERMAL POWER PLANT |  |  |  |  | DATE: | 19-Feb-2018
[5 empty] | CONDITION: | T-2 100% Load
ESP FLUE GAS MEASUREMENT DATA SHEET
DUST CONCENTRATION
Gas direction
| INLET - Duct A |  |  | INLET - Duct B
| Average | g/m3N |  | Average |  |  | g/m3N
Gas direction
| OUTLET - Duct A |  |  | OUTLET - Duct B
| Average | g/m3N |  | Average |  |  | g/m3N
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
32.9
27.5
37.0
27.9
28.1
27.1
0.0696
―
0.0696
28.1
32.6
29.2
36.2
27.8
29.7

## DUST-RESULT-3
THAI BINH 2 THERMAL POWER PLANT |  |  |  |  | DATE: | 19-Feb-2018
[5 empty] | CONDITION: | T-3 100% Load
ESP FLUE GAS MEASUREMENT DATA SHEET
DUST CONCENTRATION
Gas direction
| INLET - Duct A |  |  | INLET - Duct B
| Average | g/m3N |  | Average |  |  | g/m3N
Gas direction
| OUTLET - Duct A |  |  | OUTLET - Duct B
| Average | g/m3N |  | Average |  |  | g/m3N
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
32.9
27.5
37.0
27.9
28.1
27.1
0.0379
―
0.0379
28.1
32.6
29.2
36.2
27.8
29.7

## Measurement Act (hidden)
0 | 611.21 | 0.61121 |  | Measuring objects | Measuring method 1,JIS number | Measuring method 2
|  |  | 0 |  | blank as below
1 | 657.08 | 0.65708 | 1 | Dust concentration | JIS Z 8808(2013) | (Circular filter paper)
|  |  | 2 | Dust concentration | JIS Z 8808(2013) | (Cylinder filter paper)
2 | 705.97 | 0.70597 | 3 | Sulfur oxides concentration | JIS K 0103(2011)-7.1 | Ion chromatography
|  |  | 4 | Sulfur oxides concentration | JIS K 0103(2011)-7.2 | Precipitation titrimetry (arsenazoⅢmethod)
3 | 758.06 | 0.75806 | 5 | Sulfur oxides concentration | JIS K 0103(2011)-8 | Automated measuring method
|  |  | 6 | Sulfur oxides concentration | JIS K 0103(2011)-Annex JA (normative) | Turbidimetry (light scattering method)
4 | 813.52 | 0.81352 | 7 | Nitrogen oxides concentration | JIS K 0104(2011)-7.1 | Zinc reduction naphthyethylenediamine absorptiometry (Zn-NEDA method)
|  |  | 8 | Nitrogen oxides concentration | JIS K 0104(2011)-7.3 | Ion chromatography
5 | 872.54 | 0.87254 | 9 | Nitrogen oxides concentration | JIS K 0104(2011)-7.4 | Phenol disulfonic acid absorptiometry (PDS method)
|  |  | 10 | Nitrogen oxides concentration | JIS K 0104(2011)-7.5 | Saltzman absorptiometry
6 | 935.31 | 0.93531 | 11 | Nitrogen oxides concentration | JIS K 0104(2011)-8 | Automated measuring method：Chemiluminescence method
|  |  | 12 | Oxygen concentration | JIS K 0301(1998)-5.1 | Chemical analysis：Orsat
7 | 1002 | 1.002 | 13 | Oxygen concentration | JIS K 0301(1998)-6 | Automated measuring method：Zirconia
|  |  | 14 | Oxygen concentration | JIS K 0301(1998)-6 | Automated measuring method：Magnetic force
8 | 1072.9 | 1.0729 | 15 | Ammonia concentration | JIS K 0099(2004)-7.1 | Indophenol blue absorption spectrophotometry
|  |  | 16 | Ammonia concentration | JIS K 0099(2004)-7.2 | Gas chromatography
9 | 1148.2 | 1.1482 | 17 | Fluorine concentration | JIS K 0105(1998)-6.1 | Lanthanum-Alizarin complexone absorptiometry
|  |  | 18 | Hydrogen fluoride concentration | JIS K 0105(1998)-6.1 | Lanthanum-Alizarin complexone absorptiometry
10 | 1228.1 | 1.2281 | 19 | Chlorine concentration | JIS K 0106(2010)-7.1 | ABTS
|  |  | 20 | Chlorine concentration | JIS K 0106(2010)-7.2 | PCP
11 | 1312.9 | 1.3129 | 21 | Chlorine concentration | JIS K 0106(2010)-7.3 | Ion chromatography
|  |  | 22 | Chlorine concentration | JIS K 0106(2010)-Annex A (normative) | o－Tolidine colorimetry
12 | 1402.8 | 1.4028 | 23 | Hydrogen chloride concentration | JIS K 0107(2002)-7.1 | Ion chromatography
|  |  | 24 | Hydrogen chloride concentration | JIS K 0107(2002)-7.2 | Silver-nitrate titration method
13 | 1498 | 1.498 | 25 | Hydrogen chloride concentration | JIS K 0107(2002)-Annex D (normative) | Mercury (Ⅱ) thiocyanate absorptiometry
|  |  | 26 | Carbon monoxide concentration | JIS K 0098(1998)-5 | Gas chromatography
14 | 1598.9 | 1.5989 | 27 | Carbon monoxide concentration | JIS K 0098(1998)-6 | Detection tube
|  |  | 28 | Carbon monoxide concentration | JIS K 0098(1998)-7 | Infrared absorption spectrophotometry
15 | 1705.7 | 1.7057 | 29 | Hydrogen sulfide concentration | JIS K 0108(2010)-8 | Gas chromatography
|  |  | 30 | Hydrogen sulfide concentration | JIS K 0108(2010)-9 | Methylene blue absorptiometry
16 | 1818.7 | 1.8187 | 31 | Hydrogen cyanide concentration | JIS K 0109(1998)-6 | Gas chromatography
|  |  | 32 | Hydrogen cyanide concentration | JIS K 0109(1998)-7 | 4-Pyridinecarboxylate-pyrazolone absorptiometry
17 | 1938.3 | 1.9383 | 33 | Cadmium concentration | JIS K 0083(2006)-7.1 | Flame atomic absorption spectrometry
|  |  | 34 | Cadmium concentration | JIS K 0083(2006)-7.3 | ICP atomic emission spectroscopy
18 | 2064.7 | 2.0647 | 35 | Cadmium concentration | JIS K 0083(2006)-7.4 | ICP mass spectrometry
|  |  | 36 | Lead concentration | JIS K 0083(2006)-8.1 | Flame atomic absorption spectrometry
19 | 2198.2 | 2.1982 | 37 | Lead concentration | JIS K 0083(2006)-8.3 | ICP atomic emission spectroscopy
|  |  | 38 | Lead concentration | JIS K 0083(2006)-8.4 | ICP mass spectrometry
20 | 2339.2 | 2.3392 | 39 | Nickel concentration | JIS K 0083(2006)-9.1 | Dimethylglyoxime absorptiometry
|  |  | 40 | Nickel concentration | JIS K 0083(2006)-9.2 | Flame atomic absorption spectrometry
21 | 2488.2 | 2.4882 | 41 | Nickel concentration | JIS K 0083(2006)-9.4 | ICP atomic emission spectroscopy
|  |  | 42 | Nickel concentration | JIS K 0083(2006)-9.5 | ICP mass spectrometry
22 | 2645.3 | 2.6453 | 43 | Manganese concentration | JIS K 0083(2006)-10.1 | Periodic acid absorptiometry
|  |  | 44 | Manganese concentration | JIS K 0083(2006)-10.2 | Flame atomic absorption spectrometry
23 | 2811 | 2.811 | 45 | Manganese concentration | JIS K 0083(2006)-10.4 | ICP atomic emission spectroscopy
|  |  | 46 | Manganese concentration | JIS K 0083(2006)-10.5 | ICP mass spectrometry
24 | 2985.8 | 2.9858 | 47 | Vanadium concentration | JIS K 0083(2006)-11.1 | N-Phenylbenzohydroxamic acid absorptiometry
|  |  | 48 | Vanadium concentration | JIS K 0083(2006)-11.2 | Flame atomic absorption spectrometry
25 | 3169.9 | 3.1699 | 49 | Vanadium concentration | JIS K 0083(2006)-11.4 | ICP atomic emission spectroscopy
|  |  | 50 | Vanadium concentration | JIS K 0083(2006)-11.5 | ICP mass spectrometry
26 | 3363.9 | 3.3639 | 51 | Chromium concentration | JIS K 0083(2006)-12.1 | Diphenylcarbazide absorptiometry
|  |  | 52 | Chromium concentration | JIS K 0083(2006)-12.2 | Flame atomic absorption spectrometry
27 | 3568.1 | 3.5681 | 53 | Chromium concentration | JIS K 0083(2006)-12.4 | ICP atomic emission spectroscopy
|  |  | 54 | Chromium concentration | JIS K 0083(2006)-12.5 | ICP mass spectrometry
28 | 3783.1 | 3.7831 | 55 | Beryllium concentration | JIS K 0083(2006)-13.1 | Flame atomic absorption spectrometry
|  |  | 56 | Beryllium concentration | JIS K 0083(2006)-13.3 | ICP atomic emission spectroscopy
29 | 4009.2 | 4.0092 | 57 | Beryllium concentration | JIS K 0083(2006)-13.4 | ICP mass spectrometry
|  |  | 58 | Arsenic concentration | JIS K 0083(2006)-14.1 | Silver diethyldithiocarbamate spectrophotometric method
30 | 4247 | 4.247 | 59 | Arsenic concentration | JIS K 0083(2006)-14.2 | Atomic absorption spectrometry by hydride
|  |  | 60 | Arsenic concentration | JIS K 0083(2006)-14.4 | ICP atomic emission spectroscopy by hydride
31 | 4497 | 4.497 | 61 | Arsenic concentration | JIS K 0083(2006)-14.5 | ICP mass spectrometry
|  |  | 62 | Selenium concentration | JIS K 0083(2006)-15.1 | 3,3'-Diaminobenzidine absorptiometry
32 | 4759.7 | 4.7597 | 63 | Selenium concentration | JIS K 0083(2006)-15.2 | Atomic absorption spectrometry by hydride
|  |  | 64 | Selenium concentration | JIS K 0083(2006)-15.5 | ICP atomic emission spectroscopy by hydride
33 | 5035.6 | 5.0356 | 65 | Selenium concentration | JIS K 0083(2006)-15.6 | ICP mass spectrometry
|  |  | 66 | Bromine concentration | JIS K 0085(1998)-6.1 | Iodemetry
34 | 5325.2 | 5.3252 | 67 | Bromine concentration | JIS K 0085(1998)-6.2 | Mercury (Ⅱ) thiocyanate absorptiometry
|  |  | 68 | Phenols concentration | JIS K 0086(1998)-5.1 | Gas chromatography
35 | 5629.2 | 5.6292 | 69 | Phenols concentration | JIS K 0086(1998)-5.2 | 4 -aminoantipyrine absorptiometry
|  |  | 70 | Phenols concentration | JIS K 0086(1998)-5.3 | Ultraviolet spectrophotometry
36 | 5948.1 | 5.9481 | 71 | Pyridine concentration | JIS K 0087(1998)-5.1 | Diaminostibenedisulfonic acid absorptiometry
|  |  | 72 | Pyridine concentration | JIS K 0087(1998)-5.2 | Gas chromatography
37 | 6282.5 | 6.2825 | 73 | Benzene concentration | JIS K 0088(1997)-6.1 | Gas chromatography
|  |  | 74 | Benzene concentration | JIS K 0088(1997)-6.2 | Dinitrobenzene absorptiometry
38 | 6633.1 | 6.6331 | 75 | Acrolein concentration | JIS K 0089(1998)-5.1 | Gas chromatography
|  |  | 76 | Acrolein concentration | JIS K 0089(1998)-5.2 | Hexylresorcinol absorptiometry
39 | 7000.5 | 7.0005 | 77 | Phosgene concentration | JIS K 0090(1998) | 1,3-Diphenylurea ultraviolet spectrophotometric method
|  |  | 78 | Carbon disulfide concentration | JIS K 0091(1998)-5.1 | Copper diethyldithiocarbamate absorptiometry
40 | 7385.3 | 7.3853 | 79 | Carbon disulfide concentration | JIS K 0091(1998)-5.2 | Gas chromatography
|  |  | 80 | Mercaptan concentration | JIS K 0092(1998)-5.1 | N,N'-Ditolyl-p-phenylenediamine
41 | 7788.2 | 7.7882 | 81 | Mercaptan concentration | JIS K 0092(1998)-5.2 | Gas chromatography
|  |  | 82 | Mercury concentration | JIS K 0222(1997)-5 | Wet absorption－Reduced vaporized atomic absorption spectroscopy
42 | 8210 | 8.21 | 83 | Mercury concentration | JIS K 0222(1997)-6 | Gold amalgam collection－heating reduced vaporized atomic absorption spectroscopy
|  |  | 84 | Formaldehyde concentration | JIS K 0303(2004)-6.1 | AHMT absorptiometry
43 | 8651.3 | 8.6513 | 85 | Formaldehyde concentration | JIS K 0303(2004)-6.2 | DNPH－GC
|  |  | 86 | Formaldehyde concentration | JIS K 0303(2004)-6.5 | DNPH－HPLC
44 | 9112.9 | 9.1129 | 87 | Formaldehyde concentration | JIS K 0303(2004)-Annex (normative) | Chromotropic acid absorptiometry
|  |  | 88 | Trichloroethylene and Tetrachloroethylene concentration | JIS K 0305(1997) | GC／FID
45 | 9595.6 | 9.5956 | 89 | Trichloroethylene and Tetrachloroethylene concentration | JIS K 0305(1997) | GC／ECD
46 | 10100 | 10.1
47 | 10627 | 10.627
48 | 11178 | 11.178
49 | 11753 | 11.753
50 | 12353 | 12.353
51 | 12979 | 12.979
52 | 13632 | 13.632
53 | 14313 | 14.313
54 | 15023 | 15.023
55 | 15763 | 15.763
56 | 16534 | 16.534
57 | 17337 | 17.337
58 | 18173 | 18.173
59 | 19043 | 19.043
60 | 19948 | 19.948
61 | 20889 | 20.889
62 | 21868 | 21.868
63 | 22886 | 22.886
64 | 23944 | 23.944
65 | 25043 | 25.043
66 | 26184 | 26.184
67 | 27370 | 27.37
68 | 28600 | 28.6
69 | 29877 | 29.877
70 | 31202 | 31.202
71 | 32577 | 32.577
72 | 34002 | 34.002
73 | 35479 | 35.479
74 | 37010 | 37.01
75 | 38597 | 38.597
76 | 40240 | 40.24
77 | 41942 | 41.942
78 | 43704 | 43.704
79 | 45528 | 45.528
80 | 47416 | 47.416
81 | 49368 | 49.368
82 | 51388 | 51.388
83 | 53477 | 53.477
84 | 55636 | 55.636
85 | 57868 | 57.868
86 | 60174 | 60.174
87 | 62557 | 62.557
88 | 65017 | 65.017
89 | 67559 | 67.559
90 | 70182 | 70.182
91 | 72890 | 72.89
92 | 75685 | 75.685
93 | 78568 | 78.568
94 | 81542 | 81.542
95 | 84609 | 84.609
96 | 87771 | 87.771
97 | 91031 | 91.031
98 | 94391 | 94.391
99 | 97853 | 97.853
100 | 101419 | 101.419
100.5 | 773.68 | 103.15
101 | 787.57 | 105
101.5 | 801.66 | 106.88