## Input (hidden)
Job.No. |  |  |  | Pitot tube coefficient | C | 1 | Filter paper | Cylindrical filter paper (Silica fiber filter type 1)
Receipt number |  |  |  | Determination of SOx | Precipitation titrimetry f:factor of 5 mmol/L barium acetate solution |  | Turbidimetry k value:the inclination of a calibration curve
Atmospheric pressure |  |  |  | Determination of NOx | PDS method k value:the inclination of a calibration curve |  | NEDA method k value:the inclination of a calibration curve
Date of measurement | 2017-12-05 |  |  | Determination of HCl | Silver nitrate titrimetry f:factor of 0.1 mol/L ammonium thiocyanate solution |  | Mercury (Ⅱ) thiocyanate absorptiometry k value:the inclination of a calibration curve
Certificate number
Date of issue | -
Responsibility of measurement | 1 | Kazuyoshi Morimoto
Responsibility of the site |  | Kazuyoshi Morimoto
Fuel consumption | －
Addressee of a report 1 |  | THAI BINH 1 THERMAL POWER PLANT
Addressee of a report 2 |  | THAI BINH 1 THERMAL POWER PLANT
Place of measurement |  | ESP Inlet
Facility |  | ESP
Title of measurement |  | Measuring exhaust gas
Place of measurement (The first column) |  | My Loc Commune, Thai Thuy District, Thai Binh Province, Viet Nam
(The second column)
Facility name (Data sheet) |  | ESP
Site name of list |  | THAI BINH 1 THERMAL POWER PLANT
Type of facility |  | ESP
Measuring position |  | ESP Inlet
Sectional area of duct at measuring position m2 |  | 13.5 | 4.5m x 3.0m
Height of stack (m)
Sectional area of discharge port m2 |  |  | 4.5m x 3.0m
Date of installation
Type of fuel |  | Coal
Scale of the facility
Dust (g/m3N)
Dust On(%) |  | -
SOx On (%) |  | -
NOx (ppm)
NOx On(%) |  | -
HCl (mg/m3N)
HCL On(%)
Precauyions
For certificate
of measuring
report
For list and
data sheet
Emission
standard

## Certificate (hidden)
CERTIFICATE OF MEASUREMENT RESULT
[8 empty] | Certificate number |  |  |  |  | ： | 0
[8 empty] | Receipt number |  |  |  |  | ： | 0
[8 empty] | Date of issue |  |  |  |  | ： | -
| To: | THAI BINH 1 THERMAL POWER PLANT
[9 empty] | Company |  | ： | CHUGAI TECHNOS VIETNAM CO., LTD
| Title of measurement: |  |  | Measuring exhaust gas |  |  |  |  | Address |  | ： | 66 Cao Trieu Phat, Hung Gia 4 Area, Tan Phong Ward, District 7, Ho Chi Minh City
(ESP)
|  |  |  | ESP Inlet |  |  |  |  | Telephone |  | ： | +84-28-541 09111
[9 empty] | Fax |  | ： | +84-28-541 09222
[10 empty] | VIMCERTS No. |  |  |  |  | ： | 086
[9 empty] | Responsibility of measurement | [5 empty] | ： | Kazuyoshi Morimoto
[9 empty] | Responsibility of the site | [5 empty] | ： | Kazuyoshi Morimoto
We would like to certify measurement result which you requested as follows.
Type of samples |  |  | Flue gas |  |  |  | Type of facility | [5 empty] | ESP
Place of measurement |  |  | My Loc Commune, Thai Thuy District, Thai Binh Province, Viet Nam
-
Date of measurement |  |  | 2017-12-05
Measuring objects |  |  | Unit |  | Result of measurement |  |  | LOQ |  |  | Methods for measurement | [7 empty] | LOQ
Dust concentration |  |  | mg/Nm3 |  | Actual value | [5 empty] | JIS Z 8808:2013 Cylindrical filter paper method | [6 empty] | Vs = 0.141 | Dust (Circular filter paper) | 1mg/Corrected volume | Unit:g/m3N
|  |  | mg/Nm3 |  | Conversion value | - |  | - | [10 empty] | Dust (Cyrinder filter paper) | 5mg/Corrected volume | 3 digits after the decimal point
Sulfur oxides concentration |  |  | mg/Nm3 |  | Actual value | 1.31 |  | 1.31 |  |  | JIS K 0103:2011 -7.1 Ion chromatography method | [7 empty] | HCl | 0.6mg/m3N
|  |  | mg/Nm3 |  | Conversion value | - |  | - | [11 empty] | 0.4ppm
Sulfur dioxide concentration |  |  | mg/Nm3 |  | Average value | 26.2 |  | 26.2 |  |  | JIS B 7981:2002 Non-dispersive infrared absorption method | [7 empty] | SOx | 0.5ppm
|  |  | mg/Nm3 |  | Conversion value | - |  | - | [10 empty] | NOx | 4ppm
Nitrogen oxides concentration |  |  | mg/Nm3 |  | Actual value | 7.52 |  | 7.52 |  |  | JIS K 0104:2011 -7.3 Ion chromatography method
|  |  | mg/Nm3 |  | Conversion value | - |  | -
Nitrogen oxides concentration |  |  | mg/Nm3 |  | Average value | 9.4 |  | 9.4 |  |  | JIS B 7982:2002 Chemiluminescence method
|  |  | mg/Nm3 |  | Conversion value | - |  | -
Carbon monoxide concentration |  |  | mg/Nm3 |  | Average value | 11.4 |  | 11.4 |  |  | JIS B 7987:2006 Non-dispersive infrared absorption method
|  |  | mg/Nm3 |  | Conversion value | - |  | -
Carbon dioxide concentration |  |  | vol% |  | Average value | 0 |  | - |  |  | JIS B 7986:2006 Non-dispersive infrared absorption method
Oxygen concentration |  |  | vol% |  | Average value | 0 |  | - |  |  | JIS B 7983:1994 Magnetic method
Special note:
(1) Units of volume are under standard condition (25℃,101.32kPa). (2) Refer to table of measurement result in next page relating to general items such as flow rate etc which show flue gas property.
Address and name of company that carried out specific processes or some parts of measuring process.
―――
The items not covered by Measurement Certification under Article 107 of Japanese Measurement Act.
――― | [18 empty] | Conversion value is not covered by Measurement Certification under Article 107 of Japanese Measurement Act.
Please do not reprint a part of this certificate without permission.

## Table (hidden)
TABLE OF MEASUREMENT RESULT
Place of measurement |  |  |  | THAI BINH 1 THERMAL POWER PLANT
Facility and measuring position |  |  |  | ESP ESP Inlet
Measuring date and Measuring time |  |  |  | 2017-12-05 | 09:25～14:15
Items |  | Mark | Unit | Measurement result | Emission standard
Flow rate of wet flue gas |  | Q | m3/h |  | -
Flow rate of dry flue gas |  | Q' | m3/h |  | -
Flow velocity |  | ｖ | m/s |  | -
Temperature of flue gas |  | θs | ℃ |  | -
Static pressure of flue gas |  | Ps | Pa |  | -
Gas composition |  | CO2 | vol％ |  | -
|  | O2 | vol％ |  | -
|  | CO | vol％ |  | -
|  | N2 | vol％ |  | -
Moisture content |  | Xw | vol％ |  | -
Dust concentration | Actual value | Cs | mg/Nm3 |  | 200
| Conversion value | C | mg/Nm3
Sulfur oxides concentration | Actual value | Cs | mg/Nm3 |  | 500
| Conversion value | C | mg/Nm3
Sulfur dioxide concentration (Continuous measuring method) | Average value | Cs | mg/Nm3
| Conversion value | C | mg/Nm3
Sulfur oxides emission amount |  | Cs | mg/Nm3 |  | 850
Nitrogen oxides concentration | Actual value | Cs | mg/Nm3 |  | 850
| Conversion value | C | mg/Nm3
Nitrogen oxides concentration (Continuous measuring method) | Average value | Cs | mg/Nm3
| Conversion value | C | mg/Nm3
Carbon monoxide concentration (Continuous measuring method) | Average value | Cs | mg/Nm3 |  | 1000
| Conversion value | C | mg/Nm3
Carbon dioxide concentration (Continuous analysis method) | Conversion value | Cs | vol% |  | -
Oxygen concentration (Continuous analysis method) | Conversion value | Os | vol% |  | -
Type of facility： |  | ESP
Note: The unit represent the standard condition (25℃,101.32kPa).

## Fig (hidden)
DRAWING OF MEASURING POINT MEASURING LOCATION
Diagram 1: Measuring position
Diagram 2: Detailed measurement point drawing
Gas direction
|  | Diameter of duct 2R (m): |  | 1.3
Distance from center of duct to measuring point (m)
|  | r1( 0.500R)= |  | 0.325
|  | r2 (0.866R)= |  | 0.563
|  | Sectional area of duct at measuring position A (m) |  |  | 1.33
900
900
900
900
450
500
1000
1000
A
B
C
D
E
4500
3000

## Drawing
THAI BINH 1 THERMAL POWER PLANT
DRAWING OF MEASURING POINT
ESP
Gas direction
| INLET - Duct A |  | INLET - Duct B
Gas direction
| OUTLET - Duct A |  | OUTLET - Duct B
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000

## IN-A
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-12 | [10 empty] | Measuring condition | [7 empty] | 300MW
Measuring position | [5 empty] | Unit 2 ESP Inlet Duct A | [10 empty] | Measuring person | [7 empty] | Dung, Tuyen
[9 empty] | Recorded by |  |  | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  | 102.8
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 11:30 |  |  |  |  | 1 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5304 |  |  |  |  | 6.7 |  |  |  | 6.8 |  | 2.34
|  |  | 11:38 |  |  |  |  | 2 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5379 |  |  |  |  | 6.8 | [5 empty] | 2.34
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | D2 －013 －090 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －002
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/Nm3
| C-2 |  | 11:28 |  |  |  |  | 14 |  |  |  |  | 5.6 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2104
|  |  | 11:48 |  |  |  |  | 14 |  |  |  |  | 5.6 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2104
|  |  | Average |  |  |  |  | 14 |  |  |  |  | 5.6 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.21
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －001
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 11:00 | [5 empty] | 162 | [5 empty] | 132 |  |  |  |  | -2 | [5 empty] | 18.9 | [5 empty] | 0.906 |  |  |  | #NAME?
| A-2 | [6 empty] | 92 | [5 empty] | 132 | [10 empty] | 14.3 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 156 | [5 empty] | 130 | [10 empty] | 18.6 | [7 empty] | QA
| B-1 | [6 empty] | 66 | [5 empty] | 130 | [10 empty] | 12.1 | [7 empty] | m3/h
| B-2 | [6 empty] | 194 | [5 empty] | 131 | [10 empty] | 20.7 | [5 empty] | ① |  | 739000
| B-3 | [6 empty] | 64 | [5 empty] | 127 | [10 empty] | 11.9 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 68 | [5 empty] | 125 | [10 empty] | 12.3 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 82 | [5 empty] | 124 | [10 empty] | 13.5 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 78 | [5 empty] | 124 | [10 empty] | 13.1 | [7 empty] | Nm3/h
| D-1 | [6 empty] | 52 | [5 empty] | 118 | [10 empty] | 10.7 | [5 empty] | ① |  | 553000
| D-2 | [6 empty] | 166 | [5 empty] | 116 | [10 empty] | 19.1 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 62 | [5 empty] | 116 | [10 empty] | 11.7 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 134 | [5 empty] | 115 | [10 empty] | 17.2 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 102 | [5 empty] | 115 | [10 empty] | 15 | [7 empty] | Nm3/h
| E-3 | 11:21 | [5 empty] | 154 | [5 empty] | 115 | [10 empty] | 18.4 | [5 empty] | ① |  | 516000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 123 |  | #DIV/0! | [8 empty] | 15.2 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 003 |  |  |  | Thermometer | [7 empty] | DVM － 010 －004
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －020
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －024
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical department | [5 empty] | MM-G-01.01 | [6 empty] | Enacted date | [5 empty] | 2018-01-17

## IN-B
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-12 | [10 empty] | Measuring condition | [7 empty] | 300MW
Measuring position | [5 empty] | Unit 2 ESP Inlet Duct B | [10 empty] | Measuring person | [7 empty] | Dung, Tuyen
[9 empty] | Recorded by |  |  | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  | 102.8
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 12:20 |  |  |  |  | 3 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5397 |  |  |  |  | 6.8 |  |  |  | 6.8 |  | 2.34
|  |  | 12:27 |  |  |  |  | 7 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5355 |  |  |  |  | 6.7 | [5 empty] | 2.34
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | D2 －013 －085 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －007
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/Nm3
| C-2 |  | 12:19 |  |  |  |  | 14.2 |  |  |  |  | 5.4 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2113
|  |  | 12:34 |  |  |  |  | 14.2 |  |  |  |  | 5.4 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2113
|  |  | Average |  |  |  |  | 14.2 |  |  |  |  | 5.4 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.21
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －001
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 12:00 | [5 empty] | 144 | [5 empty] | 115 |  |  |  |  | -2.2 | [5 empty] | 17.9 | [5 empty] | 0.9 |  |  |  | #NAME?
| A-2 | [6 empty] | 86 | [5 empty] | 115 | [10 empty] | 13.8 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 152 | [5 empty] | 115 | [10 empty] | 18.4 | [7 empty] | QA
| B-1 | [6 empty] | 48 | [5 empty] | 119 | [10 empty] | 10.3 | [7 empty] | m3/h
| B-2 | [6 empty] | 182 | [5 empty] | 118 | [10 empty] | 20.1 | [5 empty] | ① |  | 700000
| B-3 | [6 empty] | 58 | [5 empty] | 121 | [10 empty] | 11.4 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 64 | [5 empty] | 125 | [10 empty] | 11.9 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 76 | [5 empty] | 125 | [10 empty] | 13 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 54 | [5 empty] | 127 | [10 empty] | 11 | [7 empty] | Nm3/h
| D-1 | [6 empty] | 58 | [5 empty] | 132 | [10 empty] | 11.4 | [5 empty] | ① |  | 520000
| D-2 | [6 empty] | 166 | [5 empty] | 132 | [10 empty] | 19.2 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 68 | [5 empty] | 128 | [10 empty] | 12.3 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 94 | [5 empty] | 135 | [10 empty] | 14.5 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 86 | [5 empty] | 135 | [10 empty] | 13.8 | [7 empty] | Nm3/h
| E-3 | 12:18 | [5 empty] | 138 | [5 empty] | 132 | [10 empty] | 17.5 | [5 empty] | ① |  | 485000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 125 |  | #DIV/0! | [8 empty] | 14.4 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 003 |  |  |  | Thermometer | [7 empty] | DVM － 010 －004
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －020
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －024
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical department | [5 empty] | MM-G-01.01 | [6 empty] | Enacted date | [5 empty] | 2018-01-17

## OUT-A
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-12 | [10 empty] | Measuring condition | [7 empty] | 300MW
Measuring position | [5 empty] | Unit 2 ESP Outlet Duct A | [10 empty] | Measuring person | [7 empty] | Hoai, Khanh, Anh
[9 empty] | Recorded by |  |  | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  | 102.8
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 11:18 |  |  |  |  | 11 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5627 |  |  |  |  | 7 |  |  |  | 7 |  | 2.34
|  |  | 11:26 |  |  |  |  | 12 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5602 |  |  |  |  | 7 | [5 empty] | 2.34
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | DVM －013 －004 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －010
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/Nm3
| C-2 |  | 11:14 |  |  |  |  | 14.2 |  |  |  |  | 5.4 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2103
|  |  | 11:34 |  |  |  |  | 14.2 |  |  |  |  | 5.4 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2103
|  |  | Average |  |  |  |  | 14.2 |  |  |  |  | 5.4 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.21
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －003
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 11:00 | [5 empty] | 102 | [5 empty] | 129 |  |  |  |  | -2.3 | [5 empty] | 15 | [5 empty] | 0.901 |  |  |  | #NAME?
| A-2 | [6 empty] | 95 | [5 empty] | 128 | [10 empty] | 14.5 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 105 | [5 empty] | 124 | [10 empty] | 15.3 | [7 empty] | QA
| B-1 | [6 empty] | 94 | [5 empty] | 130 | [10 empty] | 14.4 | [7 empty] | m3/h
| B-2 | [6 empty] | 126 | [5 empty] | 125 | [10 empty] | 16.7 | [5 empty] | ① |  | 719000
| B-3 | [6 empty] | 94 | [5 empty] | 119 | [10 empty] | 14.4 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 100 | [5 empty] | 129 | [10 empty] | 14.9 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 96 | [5 empty] | 125 | [10 empty] | 14.6 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 101 | [5 empty] | 118 | [10 empty] | 15 | [7 empty] | Nm3/h
| D-1 | [6 empty] | 94 | [5 empty] | 126 | [10 empty] | 14.4 | [5 empty] | ① |  | 536000
| D-2 | [6 empty] | 119 | [5 empty] | 122 | [10 empty] | 16.3 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 95 | [5 empty] | 119 | [10 empty] | 14.5 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 102 | [5 empty] | 123 | [10 empty] | 15 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 78 | [5 empty] | 120 | [10 empty] | 13.2 | [7 empty] | Nm3/h
| E-3 | 11:20 | [5 empty] | 90 | [5 empty] | 118 | [10 empty] | 14.1 | [5 empty] | ① |  | 498000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 124 |  | #DIV/0! | [8 empty] | 14.8 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 004 |  |  |  | Thermometer | [7 empty] | DVM － 010 －005
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －024
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －026
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical department | [5 empty] | MM-G-01.01 | [6 empty] | Enacted date | [5 empty] | 2018-01-17

## OUT-B
MEASURING DATA SHEET (1) | [13 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [5 empty] | 2018-02-12 | [10 empty] | Measuring condition | [7 empty] | 300MW
Measuring position | [5 empty] | Unit 2 ESP Outlet Duct B | [10 empty] | Measuring person | [7 empty] | Hoai, Khanh, Anh
[9 empty] | Recorded by |  |  | Calculated by |  |  | Checked by |  | PC Input |  |  | Collated by
| MOISTURE CONTENT IN FLUE GAS | [22 empty] | Atmospheric pressure | [7 empty] | Pa |  | kPa |  | 102.8
| Measuring point |  | Measuring time |  |  |  |  | U - tube No. |  |  |  | Gas meter | [13 empty] | Mass of moisture |  |  |  |  | Moisture content
[12 empty] | Suction volume | [5 empty] | Temp. |  |  | Pressure | [9 empty] | Value |  |  |  | Average
[12 empty] | V | [5 empty] | θm |  |  | Pm |  |  |  |  | m |  |  |  |  | Xw |  |  |  | Xw
[12 empty] | L | [5 empty] | ℃ |  |  | kPa |  |  |  |  | g |  |  |  |  | vol% |  |  |  | vol%
| C-2 |  | 12:02 |  |  |  |  | 13 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5485 |  |  |  |  | 6.9 |  |  |  | 6.8 |  | 2.34
|  |  | 12:09 |  |  |  |  | 14 |  |  |  | 10 | [5 empty] | 20 |  |  | 0 |  |  |  |  | 0.5369 |  |  |  |  | 6.7 | [5 empty] | 2.34
#N/A
| Equipment No. |  | Gas meter |  |  |  |  | DVM －013 －003 | [12 empty] | Suction pump | [7 empty] | DVM － 027 －009
|  |  | Barometer |  |  |  |  | DVM －016 －004
| COMPOSITION AND DENSITY OF FLUE GAS | [26 empty] | Density of wet flue gas in standard condition
| Measuring point |  | Measuring time |  |  |  |  | Gas composition
[8 empty] | CO2 |  |  |  |  | O2 |  |  |  | CO | [5 empty] | N2 |  |  |  |  | ρ0
[8 empty] | vol% |  |  |  |  | vol% |  |  |  | vol% | [5 empty] | vol% |  |  |  |  | kg/Nm3
| C-2 |  | 12:00 |  |  |  |  | 14 |  |  |  |  | 5.6 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2104
|  |  | 12:18 |  |  |  |  | 14.2 |  |  |  |  | 5.4 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.2113
|  |  | Average |  |  |  |  | 14.1 |  |  |  |  | 5.5 |  |  |  | - | [5 empty] | 80.4 |  |  |  |  | 1.21
| Equipment No. |  | Orsat apparatus |  |  |  |  | DVM －045 －003
VELOCITY AND FLOW RATE OF FLUE GAS
| Measuring point | Measuring time | [5 empty] | Dynamic pressure | [5 empty] | Temperature |  |  |  |  | Static pressure | [5 empty] | Velocity | [5 empty] | Gas density
[8 empty] | Pd | [5 empty] | θs |  |  |  |  | Ps | [5 empty] | v | [5 empty] | ρ
[8 empty] | Pa | [5 empty] | ℃ |  |  |  |  | kPa | [5 empty] | m/s | [5 empty] | kg/m3
|  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  | ② |  |  | ① |  |  |  | ②
| A-1 | 11:45 | [5 empty] | 110 | [5 empty] | 123 |  |  |  |  | -2.5 | [5 empty] | 15.6 | [5 empty] | 0.899 |  |  |  | #NAME?
| A-2 | [6 empty] | 97 | [5 empty] | 120 | [10 empty] | 14.7 | [5 empty] | Gas flow rate
| A-3 | [6 empty] | 110 | [5 empty] | 119 | [10 empty] | 15.6 | [7 empty] | QA
| B-1 | [6 empty] | 105 | [5 empty] | 126 | [10 empty] | 15.3 | [7 empty] | m3/h
| B-2 | [6 empty] | 125 | [5 empty] | 122 | [10 empty] | 16.7 | [5 empty] | ① |  | 748000
| B-3 | [6 empty] | 98 | [5 empty] | 119 | [10 empty] | 14.8 | [5 empty] | ② |  | #DIV/0!
| C-1 | [6 empty] | 109 | [5 empty] | 129 | [10 empty] | 15.6 | [5 empty] | Average |  | #DIV/0!
| C-2 | [6 empty] | 96 | [5 empty] | 125 | [10 empty] | 14.6 | [5 empty] | Wet |  | QN
| C-3 | [6 empty] | 103 | [5 empty] | 119 | [10 empty] | 15.1 | [7 empty] | Nm3/h
| D-1 | [6 empty] | 91 | [5 empty] | 130 | [10 empty] | 14.2 | [5 empty] | ① |  | 556000
| D-2 | [6 empty] | 125 | [5 empty] | 127 | [10 empty] | 16.7 | [5 empty] | ② |  | #DIV/0!
| D-3 | [6 empty] | 90 | [5 empty] | 121 | [10 empty] | 14.1 | [5 empty] | Average |  | #DIV/0!
| E-1 | [6 empty] | 123 | [5 empty] | 129 | [10 empty] | 16.5 | [5 empty] | Dry |  | Q'N
| E-2 | [6 empty] | 108 | [5 empty] | 129 | [10 empty] | 15.5 | [7 empty] | Nm3/h
| E-3 | 12:05 | [5 empty] | 114 | [5 empty] | 122 | [10 empty] | 15.9 | [5 empty] | ① |  | 518000
[31 empty] | ② |  | #DIV/0!
[8 empty] | Average | [5 empty] | 124 |  | #DIV/0! | [8 empty] | 15.4 |  |  | #DIV/0! |  |  | Average |  | #DIV/0!
| Pitot tube co-efficient | [5 empty] | C |  |  | 1 |  |  |  | Cross-sectional area | [12 empty] | A |  |  | m2 |  | 13.5
| Equipment No. |  | Manostar gauge |  |  |  |  | DVM － |  |  | 023 |  |  | － | 004 |  |  |  | Thermometer | [7 empty] | DVM － 010 －005
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Sheathed thermocouple | [7 empty] | DVM － 172 －024
[8 empty] | DVM － | [5 empty] | － |  |  |  |  | Pitot tube | [7 empty] | CVM － 018 －026
| Retention period |  |  | 5 years |  |  |  |  | Storage department | [5 empty] | Technical department | [5 empty] | MM-G-01.01 | [6 empty] | Enacted date | [5 empty] | 2018-01-17

## Dust IN-A
MEASURING DATA SHEET (2) | [14 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-12 | [11 empty] | Measuring condition | [6 empty] | 300MW
Measuring position | [6 empty] | Unit 2 ESP Inlet Duct A | [11 empty] | Measuring person | [6 empty] | Dung
| DUST CONCENTRATION IN FLUE GAS | [18 empty] | Recorded by |  |  |  | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| □ | Form 1 |  | □ |  | Form 2 |  |  | ■ | Form 1 |  |  |  | □ |  | Form 2
| □ | QMA |  | □ |  | PF-020 |  |  | ■ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [11 empty] | Pa |  |  | kPa |  | 102.8
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [11 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [8 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  |  | kPa |  |  | Nm3 |  |  | g |  |  |  | g/Nm3 |  |  | g/Nm3 |  | %
| A-1~3 |  | 15:48 |  | 3 |  | 5 |  | 3 |  |  | 9 |  |  | 124 |  |  | 21 |  |  | 0.1 |  |  | 0.125 |  |  | 3.0059 |  |  |  | 24 |  |  | - |  | - |  | 2.49
| B-1~3 |  | 16:52 |  | 3 |  | 5 |  | 4 |  |  | 9 |  |  | 107 |  |  | 21 |  |  | 0.1 |  |  | 0.107 |  |  | 2.5334 |  |  |  | 23.7 |  |  | - |  | - |  | 2.49
| C-1~3 |  | 17:08 |  | 3 |  | 5 |  | 6 |  |  | 9 |  |  | 95 |  |  | 21 |  |  | 0.1 |  |  | 0.095 |  |  | 2.4203 |  |  |  | 25.5 |  |  | - |  | - |  | 2.49
| D-1~3 |  | 17:23 |  | 3 |  | 5 |  | 7 |  |  | 9 |  |  | 103 |  |  | 21 |  |  | 0.1 |  |  | 0.103 |  |  | 2.7461 |  |  |  | 26.7 |  |  | - |  | - |  | 2.49
| E-1~3 |  | 17:39 |  | 3 |  | 5 |  | 8 |  |  | 9 |  |  | 126 |  |  | 21 |  |  | 0.1 |  |  | 0.127 |  |  | 3.3466 |  |  |  | 26.4 |  |  | - |  | - |  | 2.49
[27 empty] | Average |  |  |  | 25.3 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | D2 － 013 －090 | [11 empty] | Suction pump | [6 empty] | DVM － 027 －002
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[24 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [10 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [21 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [8 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [7 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [10 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical department | [5 empty] | MM-G-02.01 |  |  |  |  | Enacted date | [6 empty] | 2018-01-17

## Dust IN-B
MEASURING DATA SHEET (2) | [14 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-12 | [11 empty] | Measuring condition | [6 empty] | 300MW
Measuring position | [6 empty] | Unit 2 ESP Inlet Duct B | [11 empty] | Measuring person | [6 empty] | Tuyen
| DUST CONCENTRATION IN FLUE GAS | [18 empty] | Recorded by |  |  |  | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| □ | Form 1 |  | □ |  | Form 2 |  |  | ■ | Form 1 |  |  |  | □ |  | Form 2
| □ | QMA |  | □ |  | PF-020 |  |  | ■ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [11 empty] | Pa |  |  | kPa |  | 102.8
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [11 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [8 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  |  | kPa |  |  | Nm3 |  |  | g |  |  |  | g/Nm3 |  |  | g/Nm3 |  | %
| A-1~3 |  | 15:48 |  | 3 |  | 5 |  | 33 |  |  | 9 |  |  | 122 |  |  | 20 |  |  | 0.1 |  |  | 0.123 |  |  | 3.9549 |  |  |  | 32.2 |  |  | - |  | - |  | 2.34
| B-1~3 |  | 16:53 |  | 3 |  | 5 |  | 34 |  |  | 9 |  |  | 106 |  |  | 20 |  |  | 0.1 |  |  | 0.107 |  |  | 2.6497 |  |  |  | 24.8 |  |  | - |  | - |  | 2.34
| C-1~3 |  | 17:09 |  | 3 |  | 6 |  | 35 |  |  | 9 |  |  | 128 |  |  | 20 |  |  | 0.1 |  |  | 0.129 |  |  | 3.0632 |  |  |  | 23.7 |  |  | - |  | - |  | 2.34
| D-1~3 |  | 17:23 |  | 3 |  | 5 |  | 36 |  |  | 9 |  |  | 106 |  |  | 20 |  |  | 0.1 |  |  | 0.107 |  |  | 2.539 |  |  |  | 23.7 |  |  | - |  | - |  | 2.34
| E-1~3 |  | 17:33 |  | 3 |  | 5 |  | 37 |  |  | 9 |  |  | 108 |  |  | 20 |  |  | 0.1 |  |  | 0.109 |  |  | 2.5656 |  |  |  | 23.5 |  |  | - |  | - |  | 2.34
[27 empty] | Average |  |  |  | 25.6 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | D2 － 013 －085 | [11 empty] | Suction pump | [6 empty] | DVM － 027 －007
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[24 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [10 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [21 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [8 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [7 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [10 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical department | [5 empty] | MM-G-02.01 |  |  |  |  | Enacted date | [6 empty] | 2018-01-17

## Dust OUT-A
MEASURING DATA SHEET (2) | [14 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-12 | [11 empty] | Measuring condition | [6 empty] | 300MW
Measuring position | [6 empty] | Unit 2 ESP Outlet Duct A | [11 empty] | Measuring person | [6 empty] | Hoai
| DUST CONCENTRATION IN FLUE GAS | [18 empty] | Recorded by |  |  |  | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| ■ | Form 1 |  | □ |  | Form 2 |  |  | □ | Form 1 |  |  |  | □ |  | Form 2
| ■ | QMA |  | □ |  | PF-020 |  |  | □ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [11 empty] | Pa |  |  | kPa |  | 102.8
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [11 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [8 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  |  | kPa |  |  | Nm3 |  |  | g |  |  |  | g/Nm3 |  |  | g/Nm3 |  | %
| A-1~3 |  | 16:54 |  | 3 |  | 5 |  | 196 |  |  | 15 |  |  | 176 |  |  | 19 |  |  | 0.1 |  |  | 0.179 |  |  | 0.01777 |  |  |  | 0.0993 |  |  | - |  | - |  | 2.2
| B-1~3 |  | 17:13 |  | 3 |  | 5 |  | 197 |  |  | 15 |  |  | 189 |  |  | 19 |  |  | 0.1 |  |  | 0.192 |  |  | 0.01843 |  |  |  | 0.096 |  |  | - |  | - |  | 2.2
| C-1~3 |  | 17:32 |  | 3 |  | 5 |  | 198 |  |  | 15 |  |  | 181 |  |  | 19 |  |  | 0.1 |  |  | 0.184 |  |  | 0.01232 |  |  |  | 0.067 |  |  | - |  | - |  | 2.2
| D-1~3 |  | 17:50 |  | 3 |  | 5 |  | 199 |  |  | 15 |  |  | 184 |  |  | 19 |  |  | 0.1 |  |  | 0.187 |  |  | 0.01434 |  |  |  | 0.0767 |  |  | - |  | - |  | 2.2
| E-1~3 |  | 18:09 |  | 3 |  | 5 |  | 200 |  |  | 15 |  |  | 169 |  |  | 19 |  |  | 0.1 |  |  | 0.171 |  |  | 0.02075 |  |  |  | 0.1213 |  |  | - |  | - |  | 2.2
[27 empty] | Average |  |  |  | 0.0921 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | DVM － 013 －004 | [11 empty] | Suction pump | [6 empty] | DVM － 027 －010
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[24 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [10 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [21 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [8 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [7 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [10 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical department | [5 empty] | MM-G-02.01 |  |  |  |  | Enacted date | [6 empty] | 2018-01-17

## Dust OUT-B
MEASURING DATA SHEET (2) | [14 empty] | Customer | [10 empty] | THAI BINH 1 THERMAL POWER PLANT
Measuring date | [6 empty] | 2018-02-12 | [11 empty] | Measuring condition | [6 empty] | 300MW
Measuring position | [6 empty] | Unit 2 ESP Outlet Duct B | [11 empty] | Measuring person | [6 empty] | Khanh, Anh
| DUST CONCENTRATION IN FLUE GAS | [18 empty] | Recorded by |  |  |  | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
| Circular filter paper | [7 empty] | Cylindrical filter paper
| ■ | Form 1 |  | □ |  | Form 2 |  |  | □ | Form 1 |  |  |  | □ |  | Form 2
| ■ | QMA |  | □ |  | PF-020 |  |  | □ | Whatman |  |  |  | □ |  | 89 |  |  | Atmospheric pressure | [11 empty] | Pa |  |  | kPa |  | 102.8
[9 empty] | □ | 89S | [8 empty] | Oxygen standard concentration | [11 empty] | On |  |  | %
| Measuring points |  | Measuring time |  | Number of points |  | Diameter of nozzle |  | Filter paper No. |  |  | Suction duration |  |  | Gas meter | [8 empty] | Suction volume at standard condition |  |  | Mass of collected dust |  |  |  | Dust concentration |  |  |  |  | Oxygen concentration
[15 empty] | Suction volume |  |  | Temp. |  |  | Pressure | [9 empty] | Measured value |  |  | Conversion value
[7 empty] | d |  |  |  |  | t |  |  | V |  |  | θm |  |  | Pm |  |  | Vs |  |  | m |  |  |  | Cs |  |  | C |  | Os
[7 empty] | mm |  |  |  |  | min |  |  | L |  |  | ℃ |  |  | kPa |  |  | Nm3 |  |  | g |  |  |  | g/Nm3 |  |  | g/Nm3 |  | %
| A-1~3 |  | 16:54 |  | 3 |  | 5 |  | 665 |  |  | 15 |  |  | 190 |  |  | 18 |  |  | 0.1 |  |  | 0.194 |  |  | 0.01273 |  |  |  | 0.0656 |  |  | - |  | - |  | 2.06
| B-1~3 |  | 17:13 |  | 3 |  | 5 |  | 666 |  |  | 15 |  |  | 190 |  |  | 18 |  |  | 0.1 |  |  | 0.194 |  |  | 0.0106 |  |  |  | 0.0546 |  |  | - |  | - |  | 2.06
| C-1~3 |  | 17:32 |  | 3 |  | 5 |  | 667 |  |  | 15 |  |  | 180 |  |  | 18 |  |  | 0.1 |  |  | 0.183 |  |  | 0.00871 |  |  |  | 0.0476 |  |  | - |  | - |  | 2.06
| D-1~3 |  | 17:50 |  | 3 |  | 5 |  | 668 |  |  | 15 |  |  | 187 |  |  | 19 |  |  | 0.1 |  |  | 0.19 |  |  | 0.01135 |  |  |  | 0.0597 |  |  | - |  | - |  | 2.2
| E-1~3 |  | 18:09 |  | 3 |  | 5 |  | 669 |  |  | 15 |  |  | 197 |  |  | 19 |  |  | 0.1 |  |  | 0.2 |  |  | 0.00741 |  |  |  | 0.0371 |  |  | - |  | - |  | 2.2
[27 empty] | Average |  |  |  | 0.0529 |  |  | - |  | -
| Equipment No. |  |  | Gas meter | [7 empty] | DVM － 013 －003 | [11 empty] | Suction pump | [6 empty] | DVM － 027 －009
|  |  |  | Orsat apparatus | [7 empty] | DVM － 045 －
[24 empty] | Calculated by |  |  | Checked by |  |  |  | PC Input |  |  | Collated by
NITROGEN OXIDE CONCENTRATION IN FLUE GAS
| Measuring point | [15 empty] | Oxygen standard concentration | [10 empty] | On |  |  |  | %
| Measuring time |  | NOx flask | [21 empty] | Suction volume at standard condition |  | Ion concentration determined from the working curve | [5 empty] | Nitrogen oxide concentration |  |  |  | Oxygen concentration
|  |  | No. |  | Before sampling | [7 empty] | After sampling | [8 empty] | Volume
[5 empty] | Absolute pressure |  |  | Temp. |  | Saturated vapor pressure |  |  | Absolute pressure |  |  |  | Temp. |  | Saturated vapor pressure | [7 empty] | NO3 |  |  | NO2 |  |  | Measured value |  | Conversion value
[5 empty] | Pi |  |  | ti |  | Pni |  |  | Pf |  |  |  | tf |  | Pnf |  |  | V-20 |  |  | Vs |  | a |  |  | b |  |  | Cs |  | C |  | Os
[5 empty] | kPa |  |  | ℃ |  | kPa |  |  | kPa |  |  |  | ℃ |  | kPa |  |  | mL |  |  | mL |  | mg/L |  |  | mg/L |  |  | ppm |  | ppm |  | %
Average
Flask (After collecting)
[9 empty] | No. |  | Atmospheric pressure | [5 empty] | Residual pressure
[11 empty] | kPa | [5 empty] | kPa
| Equipment No. |  |  | Manometer | [7 empty] | DVM － － | [10 empty] | Mighty pump | [5 empty] | DVM－ 029 －
|  |  |  | Orsat apparatus | [7 empty] | DVM － 016 －
| Retention period |  |  |  |  | 5 years |  |  |  | Storage department | [6 empty] | Technical department | [5 empty] | MM-G-02.01 |  |  |  |  | Enacted date | [6 empty] | 2018-01-17

## DUST-RESULT-1
THAI BINH 1 THERMAL POWER PLANT |  |  |  |  | DATE: | 12-Feb-2018
[5 empty] | CONDITION: | 300MW
ESP FLUE GAS MEASUREMENT DATA SHEET
DUST CONCENTRATION
Gas direction
| INLET - Duct A |  |  | INLET - Duct B
| Average | g/Nm3 |  | Average |  |  | g/Nm3
Gas direction
| OUTLET - Duct A |  |  | OUTLET - Duct B
| Average | g/Nm3 |  | Average |  |  | g/Nm3
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
900
900
900
900
450
500
1000
1000
900
900
900
900
450
500
1000
1000
A
B
C
D
E
A
B
C
D
E
4500
4500
3000
3000
23.7
25.5
26.7
24.8
23.7
23.7
0.0960
0.0670
0.0767
0.0546
0.0476
0.0597
0.0529
0.0921
25.6
25.3
24.0
26.4
23.5
0.0656
0.0371
0.1213
0.0993
32.2

## Summary Result
THAI BINH 1 THERMAL POWER PLANT | [6 empty] | DATE: | 2018-02-12
CONDITION:
FLUE GAS MEASUREMENT DATA SHEET
ESP PERFORMANCE TEST
| Item |  |  | ESP INLET |  | ESP OUTLET
|  |  |  | DUCT A | DUCT B | DUCT A |  | DUCT B
| Moisture content |  | %
| Gas temperature |  | ℃
| Gas static pressure |  | Pa
| Flow rate (wet) |  | m3N/h
| Flow rate (dry) |  | m3N/h
| Gas composition | CO2 | %
|  | O2 | %
|  | CO | %
|  | N2 | %
| Dust concentration |  | g/m3N
| Dust concentration |  | g/m3N

## Measurement Act (hidden)
0 | 611.21 | 0.61121 |  | Measuring objects | Measuring method 1,JIS number | Measuring method 2
|  |  | 0 |  | blank as below
1 | 657.08 | 0.65708 | 1 | Dust concentration | JIS Z 8808(2013) | (Circular filter paper)
|  |  | 2 | Dust concentration | JIS Z 8808(2013) | (Cylinder filter paper)
2 | 705.97 | 0.70597 | 3 | Sulfur oxides concentration | JIS K 0103(2011)-7.1 | Ion chromatography
|  |  | 4 | Sulfur oxides concentration | JIS K 0103(2011)-7.2 | Precipitation titrimetry (arsenazoⅢmethod)
3 | 758.06 | 0.75806 | 5 | Sulfur oxides concentration | JIS K 0103(2011)-8 | Automated measuring method
|  |  | 6 | Sulfur oxides concentration | JIS K 0103(2011)-Annex JA (normative) | Turbidimetry (light scattering method)
4 | 813.52 | 0.81352 | 7 | Nitrogen oxides concentration | JIS K 0104(2011)-7.1 | Zinc reduction naphthyethylenediamine absorptiometry (Zn-NEDA method)
|  |  | 8 | Nitrogen oxides concentration | JIS K 0104(2011)-7.3 | Ion chromatography
5 | 872.54 | 0.87254 | 9 | Nitrogen oxides concentration | JIS K 0104(2011)-7.4 | Phenol disulfonic acid absorptiometry (PDS method)
|  |  | 10 | Nitrogen oxides concentration | JIS K 0104(2011)-7.5 | Saltzman absorptiometry
6 | 935.31 | 0.93531 | 11 | Nitrogen oxides concentration | JIS K 0104(2011)-8 | Automated measuring method：Chemiluminescence method
|  |  | 12 | Oxygen concentration | JIS K 0301(1998)-5.1 | Chemical analysis：Orsat
7 | 1002 | 1.002 | 13 | Oxygen concentration | JIS K 0301(1998)-6 | Automated measuring method：Zirconia
|  |  | 14 | Oxygen concentration | JIS K 0301(1998)-6 | Automated measuring method：Magnetic force
8 | 1072.9 | 1.0729 | 15 | Ammonia concentration | JIS K 0099(2004)-7.1 | Indophenol blue absorption spectrophotometry
|  |  | 16 | Ammonia concentration | JIS K 0099(2004)-7.2 | Gas chromatography
9 | 1148.2 | 1.1482 | 17 | Fluorine concentration | JIS K 0105(1998)-6.1 | Lanthanum-Alizarin complexone absorptiometry
|  |  | 18 | Hydrogen fluoride concentration | JIS K 0105(1998)-6.1 | Lanthanum-Alizarin complexone absorptiometry
10 | 1228.1 | 1.2281 | 19 | Chlorine concentration | JIS K 0106(2010)-7.1 | ABTS
|  |  | 20 | Chlorine concentration | JIS K 0106(2010)-7.2 | PCP
11 | 1312.9 | 1.3129 | 21 | Chlorine concentration | JIS K 0106(2010)-7.3 | Ion chromatography
|  |  | 22 | Chlorine concentration | JIS K 0106(2010)-Annex A (normative) | o－Tolidine colorimetry
12 | 1402.8 | 1.4028 | 23 | Hydrogen chloride concentration | JIS K 0107(2002)-7.1 | Ion chromatography
|  |  | 24 | Hydrogen chloride concentration | JIS K 0107(2002)-7.2 | Silver-nitrate titration method
13 | 1498 | 1.498 | 25 | Hydrogen chloride concentration | JIS K 0107(2002)-Annex D (normative) | Mercury (Ⅱ) thiocyanate absorptiometry
|  |  | 26 | Carbon monoxide concentration | JIS K 0098(1998)-5 | Gas chromatography
14 | 1598.9 | 1.5989 | 27 | Carbon monoxide concentration | JIS K 0098(1998)-6 | Detection tube
|  |  | 28 | Carbon monoxide concentration | JIS K 0098(1998)-7 | Infrared absorption spectrophotometry
15 | 1705.7 | 1.7057 | 29 | Hydrogen sulfide concentration | JIS K 0108(2010)-8 | Gas chromatography
|  |  | 30 | Hydrogen sulfide concentration | JIS K 0108(2010)-9 | Methylene blue absorptiometry
16 | 1818.7 | 1.8187 | 31 | Hydrogen cyanide concentration | JIS K 0109(1998)-6 | Gas chromatography
|  |  | 32 | Hydrogen cyanide concentration | JIS K 0109(1998)-7 | 4-Pyridinecarboxylate-pyrazolone absorptiometry
17 | 1938.3 | 1.9383 | 33 | Cadmium concentration | JIS K 0083(2006)-7.1 | Flame atomic absorption spectrometry
|  |  | 34 | Cadmium concentration | JIS K 0083(2006)-7.3 | ICP atomic emission spectroscopy
18 | 2064.7 | 2.0647 | 35 | Cadmium concentration | JIS K 0083(2006)-7.4 | ICP mass spectrometry
|  |  | 36 | Lead concentration | JIS K 0083(2006)-8.1 | Flame atomic absorption spectrometry
19 | 2198.2 | 2.1982 | 37 | Lead concentration | JIS K 0083(2006)-8.3 | ICP atomic emission spectroscopy
|  |  | 38 | Lead concentration | JIS K 0083(2006)-8.4 | ICP mass spectrometry
20 | 2339.2 | 2.3392 | 39 | Nickel concentration | JIS K 0083(2006)-9.1 | Dimethylglyoxime absorptiometry
|  |  | 40 | Nickel concentration | JIS K 0083(2006)-9.2 | Flame atomic absorption spectrometry
21 | 2488.2 | 2.4882 | 41 | Nickel concentration | JIS K 0083(2006)-9.4 | ICP atomic emission spectroscopy
|  |  | 42 | Nickel concentration | JIS K 0083(2006)-9.5 | ICP mass spectrometry
22 | 2645.3 | 2.6453 | 43 | Manganese concentration | JIS K 0083(2006)-10.1 | Periodic acid absorptiometry
|  |  | 44 | Manganese concentration | JIS K 0083(2006)-10.2 | Flame atomic absorption spectrometry
23 | 2811 | 2.811 | 45 | Manganese concentration | JIS K 0083(2006)-10.4 | ICP atomic emission spectroscopy
|  |  | 46 | Manganese concentration | JIS K 0083(2006)-10.5 | ICP mass spectrometry
24 | 2985.8 | 2.9858 | 47 | Vanadium concentration | JIS K 0083(2006)-11.1 | N-Phenylbenzohydroxamic acid absorptiometry
|  |  | 48 | Vanadium concentration | JIS K 0083(2006)-11.2 | Flame atomic absorption spectrometry
25 | 3169.9 | 3.1699 | 49 | Vanadium concentration | JIS K 0083(2006)-11.4 | ICP atomic emission spectroscopy
|  |  | 50 | Vanadium concentration | JIS K 0083(2006)-11.5 | ICP mass spectrometry
26 | 3363.9 | 3.3639 | 51 | Chromium concentration | JIS K 0083(2006)-12.1 | Diphenylcarbazide absorptiometry
|  |  | 52 | Chromium concentration | JIS K 0083(2006)-12.2 | Flame atomic absorption spectrometry
27 | 3568.1 | 3.5681 | 53 | Chromium concentration | JIS K 0083(2006)-12.4 | ICP atomic emission spectroscopy
|  |  | 54 | Chromium concentration | JIS K 0083(2006)-12.5 | ICP mass spectrometry
28 | 3783.1 | 3.7831 | 55 | Beryllium concentration | JIS K 0083(2006)-13.1 | Flame atomic absorption spectrometry
|  |  | 56 | Beryllium concentration | JIS K 0083(2006)-13.3 | ICP atomic emission spectroscopy
29 | 4009.2 | 4.0092 | 57 | Beryllium concentration | JIS K 0083(2006)-13.4 | ICP mass spectrometry
|  |  | 58 | Arsenic concentration | JIS K 0083(2006)-14.1 | Silver diethyldithiocarbamate spectrophotometric method
30 | 4247 | 4.247 | 59 | Arsenic concentration | JIS K 0083(2006)-14.2 | Atomic absorption spectrometry by hydride
|  |  | 60 | Arsenic concentration | JIS K 0083(2006)-14.4 | ICP atomic emission spectroscopy by hydride
31 | 4497 | 4.497 | 61 | Arsenic concentration | JIS K 0083(2006)-14.5 | ICP mass spectrometry
|  |  | 62 | Selenium concentration | JIS K 0083(2006)-15.1 | 3,3'-Diaminobenzidine absorptiometry
32 | 4759.7 | 4.7597 | 63 | Selenium concentration | JIS K 0083(2006)-15.2 | Atomic absorption spectrometry by hydride
|  |  | 64 | Selenium concentration | JIS K 0083(2006)-15.5 | ICP atomic emission spectroscopy by hydride
33 | 5035.6 | 5.0356 | 65 | Selenium concentration | JIS K 0083(2006)-15.6 | ICP mass spectrometry
|  |  | 66 | Bromine concentration | JIS K 0085(1998)-6.1 | Iodemetry
34 | 5325.2 | 5.3252 | 67 | Bromine concentration | JIS K 0085(1998)-6.2 | Mercury (Ⅱ) thiocyanate absorptiometry
|  |  | 68 | Phenols concentration | JIS K 0086(1998)-5.1 | Gas chromatography
35 | 5629.2 | 5.6292 | 69 | Phenols concentration | JIS K 0086(1998)-5.2 | 4 -aminoantipyrine absorptiometry
|  |  | 70 | Phenols concentration | JIS K 0086(1998)-5.3 | Ultraviolet spectrophotometry
36 | 5948.1 | 5.9481 | 71 | Pyridine concentration | JIS K 0087(1998)-5.1 | Diaminostibenedisulfonic acid absorptiometry
|  |  | 72 | Pyridine concentration | JIS K 0087(1998)-5.2 | Gas chromatography
37 | 6282.5 | 6.2825 | 73 | Benzene concentration | JIS K 0088(1997)-6.1 | Gas chromatography
|  |  | 74 | Benzene concentration | JIS K 0088(1997)-6.2 | Dinitrobenzene absorptiometry
38 | 6633.1 | 6.6331 | 75 | Acrolein concentration | JIS K 0089(1998)-5.1 | Gas chromatography
|  |  | 76 | Acrolein concentration | JIS K 0089(1998)-5.2 | Hexylresorcinol absorptiometry
39 | 7000.5 | 7.0005 | 77 | Phosgene concentration | JIS K 0090(1998) | 1,3-Diphenylurea ultraviolet spectrophotometric method
|  |  | 78 | Carbon disulfide concentration | JIS K 0091(1998)-5.1 | Copper diethyldithiocarbamate absorptiometry
40 | 7385.3 | 7.3853 | 79 | Carbon disulfide concentration | JIS K 0091(1998)-5.2 | Gas chromatography
|  |  | 80 | Mercaptan concentration | JIS K 0092(1998)-5.1 | N,N'-Ditolyl-p-phenylenediamine
41 | 7788.2 | 7.7882 | 81 | Mercaptan concentration | JIS K 0092(1998)-5.2 | Gas chromatography
|  |  | 82 | Mercury concentration | JIS K 0222(1997)-5 | Wet absorption－Reduced vaporized atomic absorption spectroscopy
42 | 8210 | 8.21 | 83 | Mercury concentration | JIS K 0222(1997)-6 | Gold amalgam collection－heating reduced vaporized atomic absorption spectroscopy
|  |  | 84 | Formaldehyde concentration | JIS K 0303(2004)-6.1 | AHMT absorptiometry
43 | 8651.3 | 8.6513 | 85 | Formaldehyde concentration | JIS K 0303(2004)-6.2 | DNPH－GC
|  |  | 86 | Formaldehyde concentration | JIS K 0303(2004)-6.5 | DNPH－HPLC
44 | 9112.9 | 9.1129 | 87 | Formaldehyde concentration | JIS K 0303(2004)-Annex (normative) | Chromotropic acid absorptiometry
|  |  | 88 | Trichloroethylene and Tetrachloroethylene concentration | JIS K 0305(1997) | GC／FID
45 | 9595.6 | 9.5956 | 89 | Trichloroethylene and Tetrachloroethylene concentration | JIS K 0305(1997) | GC／ECD
46 | 10100 | 10.1
47 | 10627 | 10.627
48 | 11178 | 11.178
49 | 11753 | 11.753
50 | 12353 | 12.353
51 | 12979 | 12.979
52 | 13632 | 13.632
53 | 14313 | 14.313
54 | 15023 | 15.023
55 | 15763 | 15.763
56 | 16534 | 16.534
57 | 17337 | 17.337
58 | 18173 | 18.173
59 | 19043 | 19.043
60 | 19948 | 19.948
61 | 20889 | 20.889
62 | 21868 | 21.868
63 | 22886 | 22.886
64 | 23944 | 23.944
65 | 25043 | 25.043
66 | 26184 | 26.184
67 | 27370 | 27.37
68 | 28600 | 28.6
69 | 29877 | 29.877
70 | 31202 | 31.202
71 | 32577 | 32.577
72 | 34002 | 34.002
73 | 35479 | 35.479
74 | 37010 | 37.01
75 | 38597 | 38.597
76 | 40240 | 40.24
77 | 41942 | 41.942
78 | 43704 | 43.704
79 | 45528 | 45.528
80 | 47416 | 47.416
81 | 49368 | 49.368
82 | 51388 | 51.388
83 | 53477 | 53.477
84 | 55636 | 55.636
85 | 57868 | 57.868
86 | 60174 | 60.174
87 | 62557 | 62.557
88 | 65017 | 65.017
89 | 67559 | 67.559
90 | 70182 | 70.182
91 | 72890 | 72.89
92 | 75685 | 75.685
93 | 78568 | 78.568
94 | 81542 | 81.542
95 | 84609 | 84.609
96 | 87771 | 87.771
97 | 91031 | 91.031
98 | 94391 | 94.391
99 | 97853 | 97.853
100 | 101419 | 101.419
100.5 | 773.68 | 103.15
101 | 787.57 | 105
101.5 | 801.66 | 106.88