STANDARD OPERATING PROCEDURE

Online monitoring system

| MPCL-OBOP-SOP-01-013 |  |
| --- | --- |
| Approved by: | Signature: |

| Revision No. | Amendment Description: | Revision Date | Prepared by | Reviewed by |
| --- | --- | --- | --- | --- |
| 0 | First issue | Feb,1st 2018 | PHAM LE HUONG | NGUYEN DIEU |

- PURPOSE AND SCOPE

The purpose of this procedure is to provide a systematic guideline to operate  Online monitoring system, provides the hazards/ risks involved with precautions, system design limitation, operating procedure instruction for the pre start-up, start-up & shutdown of the system.

- FUNCTION OF THE SYSTEM

Online monitoring system to monitor operating conditions of discharged waste water quality, the installation of additional online environmental monitoring system is necessary. It allows the storage of online environmental quality data, help summarize monitoring results with comparison to applicable standards.

- SYSTEM HAZARDS/RISKS

- Moving/Rotating Parts

- Chemical Hazards

- Electrical Hazards

- SYSTEM DESIGN LIMITATIONS

| Description | Limitation |
| --- | --- |
| pH | 5.5-9 |
| Temperature | <400 C |
| Free clorine | <0.2 mg/l |

- PRECAUTIONS

- Tasks and activities shall be performed only by duly qualified operators.

- Clear line of communications shall be established between CBO and Local Operator.

- Chemical reagent should be handled carefully, before change chlorine reagent refer MSDS instruction.

- OPERATING PROCEDURES

| ACTIVITY/TASK | ACTION | RESPONSIBLE | LOCATION | REMARK |
| --- | --- | --- | --- | --- |
| 1. Pre start-up | - Ensure Sampling pump A ( P0GCR10AP001)/ B( P0GCR10AP002) in auto mode. - Checking sampling pump A inlet valve( P0GCR10AA001)/ outlet vavle (P0GCR10AA003) & pump B inlet valve (P0GCR10AA002/out let valve (P0GCR10AA004) in open condition. - Ensure inlet valve / outlet valve of pH sensor open condition & bypass valve close. - Check inlet valve of instrument panel online mornitoring system open. - Visual check suction strainers of sampling pump A/B clean. - Ensure chlorine reagent not empty. | BOP operator | Online monitoring system |  |
| 2. Start -up | - In HMI select pump A ( or B) in duty, click auto start pump A (or B) will run. - Open vent valve at discharge sampling pump. After water come out continuously, close vent valve. - Pump A& B will change over automatically after 5 hours. - Discharge pressure sampling pump 4-6 kg/cm2 | BOP operator | Online monitoring system |  |
| 3. Shut down | 1. Click auto stop pump A or B 2.In the case shutdown system for maintenance,local operator have to inform CCR and environment authorize | BOP operator | Online monitoring system |  |
| 4.Normal operation | 1.Monitoring system closely on DONRE 1. Check system every 4 hours, make sure have flow sample for all online instrument 2. Grab sample every week to cross check online instrument 2. Check on site system : + Free chlorine analyzer:If reagent standard for free chlorine analyzer remain 10% need to replace and recorded on logbook + Sampling pump: cleaning suction strainer if it get dirty or alarm low pressure switch at discharge pump; change pump to manual mode and stop pump, start other pump in service. Close inlet valve of strainer & sampling pump discharge valve. Open strainer to clean mud, after finished open vent valve, sampling pump discharge valve & suction valve open slowly, when water come out to vent valve continously then close vent valve. *During cleaning job strainer for sampling pump, if it effected online instrument get over limitation ,immediately inform reasonable to CCR and environment authorize | BOP operator | Online monitoring system | If have any abnormal parameter between on site monitoring system and DONRE system , local operator immediately inform to CCR and enviroment authorize |